## Doc
"UGTANK" --- UNDERGROUND STORAGE TANK ANCHORAGE DESIGN
Program Description:
"UGTANK" is a spreadsheet program written in MS-Excel for the purpose of determining the anchorage
requirement to hold down an underground storage tank. Specifically the requirements for anchor straps,
anchor rods, and turnbuckles, as well as the reinforced concrete spread foundation are determined. Tables
for rod and turnbuckle load capacities as well as strap load capacities are displayed to the right off of the main
calculation pages.
This program is a workbook consisting of two (2) worksheets, described as follows:
Worksheet Name | Description
Doc | This documentation sheet
Underground Tank Anchorage | Underground storage tank anchorage design
Program Assumptions and Limitations:
1. This program is in part based on the following two (2) dated, but still useful references:
a. Lockwood Greene Engineering Special Design Instruction No. 38,
"An Approach to the Design of Anchorages for Underground Storage Tanks", dated December 6, 1972.
b. Lockwood Greene Engineering Special Design Instruction No. 31,
"Design of Anchorage for Underground Storage Tanks", dated January 14, 1972.
2. This program utilizes the procedures and guidelines per the ACI 318-99 Building Code in the design of the
reinforcing for the concrete spread foundation.
3. This program refers to the AISC 9th Edition (ASD) Manual, 1989. The values for safe working loads for
turnbuckles are taken from the table on page 4-149 of the Manual.
4. The soil is assumed to have no voids and is assumed saturated with water (water level to top of grade), while
the tank is assumed to be empty. These conservative assumptions result in largest possible buoyant force.
5. This program permits the user to utilize either steel tension straps or threaded rods with turnbuckles to
secure the tank to the foundation. Note: if turnbuckles are used, then they will control the required threaded
rod size.
6. This program assumes that the empty tank weight is subtracted from the buoyant force in determining the
tension force in either the straps or anchor rods.
7. The program assumes that the distance between the ends of a strap or rod is equal to OD + 6".
8. The program assumes that the tank is centered on the spread foundation.
9. For the design of the foundation reinforcing in the short direction, this program assumes a uniformly loaded
simple span beam strip with cantilevers (overhangs) at each end. The ends of the anchor serve as the
supports. The assumed uniform loading on this "beam strip" is determined as 2 times the anchor tension
divided by the foundation width.
10. This program does not address the anchorage of the straps or rods to the concrete foundation. That must
be separately by the user.
11. Underground tank should be bedded on 12" of compacted sand rather than bearing directly on the concrete
spread foundation. This will protect the integrity of the tank and minimize possible failure of the tank joints.
12. Provide turnbuckles in the tank anchor straps. This allows for final adjustment. Where flat straps are used,
this will necessitate welding a round bar extension to accommodate the turnbuckle.
13. This program contains “comment boxes” which contain information including explanations of input items, etc.
(Note: presence of a “comment box” is denoted by a “red triangle” in the upper right-hand corner of a cell.
Merely move the mouse pointer to the desired cell to view the contents of that particular "comment box".)

## Underground Tank Anchorage
UNDERGROUND STORAGE TANK ANCHORAGE DESIGN | [9 empty] | CALCULATIONS: | [11 empty] | Version 1.0
For a Buried Horizontal Tank
Anchored to a Reinforced Concrete Spread Foundation | [9 empty] | Tank Outside Dimensions:
Job Name: |  |  |  | Subject: |  |  | Flat |  |  | Outside Dia., OD = | 8.0833 | ft. | OD=ID+2*(t/12)
Job Number: |  |  |  | Originator: | Checker: |  | Elliptical |  |  | Total Length, L = | 34.5 | ft. | L(total) = Lc+2*Le
[7 empty] | Spherical |  |  | Tank Surface Area:
Input Data: | [6 empty] | 0 |  |  | Flat Ends = | N.A. | ft.^2 | Ae = 2*(pi*(OD^2)/4)
[7 empty] | 1 |  |  | Elliptical Ends = | N.A. | ft.^2 | Ae = 2*((pi*(2*(OD/2)^2+Le^2/e*LN((1+e)/(1-e))))/2) ** | [9 empty] | Anchor Rod and
| Factor of Safety for Uplift, FS = | 1.5 |  |  |  |  | 1.5 |  |  | Spherical Ends = | 203.1664 | ft.^2 | Ae = 2*(pi*(OD^2+4*Le^2)/4) | [9 empty] | Turnbuckle Capacities
| Tank Inside Diameter, ID = | 8 | ft. |  |  |  | 2 |  |  | Horiz. Cylinder = | 672.9526 | ft.^2 | Ac = pi*OD*Lc | [9 empty] | Rod | Anchor | Turnbuckle
| Tank Wall Thickness, t = | 0.5 | in. |  |  |  | 2.5 |  |  | Total Surface Area, A(total) = | 876.1189 | ft.^2 | A(total) = Ac+Ae | [9 empty] | Dia. | Rod | Safe
| Tank Configuration at Ends = | Spherical |  |  |  |  | 3 | [5 empty] | ** where: e = SQRT((OD/2)^2-Le^2)/(OD/2) | [9 empty] | D | Allow. | Working
| Tank Cylinder Length, Lc = | 26.5 | ft. |  |  |  | 3.5 |  |  | Tank Empty Weight: | [12 empty] | (in.) | Load (k) | Load (k)
| Tank End Lengths, Le = | 4 | ft. |  |  |  | 4 |  |  | Flat Ends = | N.A. | kips | We = Ae*(t/12)*w | [9 empty] | 5 | 375 | 294.7
| Unit Wt. of Tank Material, w = | 100 | pcf |  |  |  | 4.5 |  |  | Elliptical Ends = | N.A. | kips | We = Ae*(t/12)*w | [9 empty] | 4.75 | 338.5 | 233.8
| Soil Dry Unit Weight, we = | 105 | pcf |  |  |  | 5 |  |  | Spherical Ends = | 0.84653 | kips | We = Ae*(t/12)*w | [9 empty] | 4.5 | 303.8 | 233.8
| Buried Depth to Top/Tank, h = | 3 | ft. |  |  |  | 5.5 |  |  | Horiz. Cylinder = | 2.804 | kips | Wc = Ac*(t/12)*w | [9 empty] | 4.25 | 271 | 233.8
| Concrete Compressive Strength, f'c = | 4 | ksi. |  |  |  | 6 |  |  | Total Empty Weight = | 4.6505 | kips | W(total) = Wc+We+Wm | [9 empty] | 4 | 240 | 167.8
| Steel Reinforcing Yield Strength, fy = | 60 | ksi. | [6 empty] | Tank Volume: | [12 empty] | 3.75 | 211 | 167.8
| Number of Risers, Nr = | 1 |  | Nomenclature | [5 empty] | Flat Ends = | N.A. | ft.^3 | Ve = 0 (for flat ends) | [9 empty] | 3.5 | 183.8 | 122.2
| Riser Inside Dia., Dr = | 3 | ft. | [6 empty] | Elliptical Ends = | N.A. | ft.^3 | Ve = 2*((4/3*pi*(ID/2)^2*(Le-t/12))/2) | [9 empty] | 3.25 | 158.4 | 122.2
| Misc. Weight (incl. Risers), Wm = | 1 | kips | Assumptions and Criteria: | [5 empty] | Spherical Ends = | 263.9155 | ft.^3 | Ve = 2*(pi*(Le-t/12)*(3*OD^2+4*(Le-t/12)^2)/24) | [9 empty] | 3 | 135 | 96.7
| Spread Foundation Length, Lf = | 28.5 | ft. | 1. Soil is saturated, with no voids, and water table at grade. | [5 empty] | Horiz. Cylinder = | 1332.0353 | ft.^3 | Vc = pi*ID^2/4*Lc | [9 empty] | 2.75 | 113.4 | 75
| Spread Foundation Width, Bf = | 12 | ft. | 2. Tank is empty and is centered on foundation. | [5 empty] | Volume of riser(s) = | 21.2058 | ft.^3 | Vr = Nr*(pi*Dr^2/4*h) | [9 empty] | 2.5 | 93.8 | 60
| Spread Foundation Thickness, Tf = | 1.5 | ft. | 3. Tension straps or rods with turnbuckles may be used. | [5 empty] | Total Volume = | 1617.1566 | ft.^3 | V(total) = Vc+Ve+Vr | [9 empty] | 2.25 | 75.9 | 48
| Anchor Strap Width, bs = | 3 | in. | 4. Distance between each end of a strap or rod = OD + 6". | [5 empty] | Uplift (Buoyant) Force: | [12 empty] | 2 | 60 | 37.2
| No. Anchor Straps/Rods Used, Na = | 4 |  | 5. 12" thick sand bed between bottom/tank and top/fdn. | [5 empty] | Flat Ends = | N.A. | kips | Ue = (62.4*Ve)/1000 (unit weight of water = 62.4 pcf) | [9 empty] | 1.875 | 52.7 | 37.2
[10 empty] | Elliptical Ends = | N.A. | kips | Ue = (62.4*Ve)/1000 | [9 empty] | 1.75 | 45.9 | 28.3
Results: | [9 empty] | Spherical Ends = | 16.4683 | kips | Ue = (62.4*Ve)/1000 | [9 empty] | 1.625 | 39.6 | 24.5
[10 empty] | Horiz. Cylinder = | 83.119 | kips | Uc = (62.4*Vc)/1000 | [9 empty] | 1.5 | 33.8 | 21
Determine Empty Weight of Tank: | [9 empty] | Uplift force on risers, Ur = | 1.3232 | kips | Ur = (62.4*Vr)/1000 | [9 empty] | 1.375 | 28.4 | 17.4
| Outside Dia., OD = | 8.0833 | ft. | OD=ID+2*(t/12) | [5 empty] | Total uplift force, U(total) = | 100.9106 | kips | U(total) = Uc+Ue+Ur | [9 empty] | 1.25 | 23.4 | 15.2
| Total Tank Length, L(total) = | 34.5 | ft. | L(total) = Lc+2*Le | [5 empty] | Weight of Soil Above Spread Foundation: | [12 empty] | 1.125 | 19 | 11.6
| Tank End Areas, Ae = | 203.1664 | ft.^2 | Ae = 2*(pi*(OD^2+4*Le^2)/4) | [5 empty] | Volume of Soil, Vs = | 2515.332 | ft.^3 | Vs = ((h+OD+1.0')*Lf*Bf)-V(total) | [9 empty] | 1 | 15 | 9.3
| Tank Cylinder Area, Ac = | 672.9526 | ft.^2 | Ac = pi*OD*Lc | [5 empty] | Buoyed Soil Unit Weight, ws = | 42.6 | pcf | ws = we-62.4 (unit weight of water = 62.4 pcf) | [9 empty] | 0.875 | 11.5 | 7.2
| Total Surface Area, A(total) = | 876.1189 | ft.^2 | A(total) = Ac+Ae | [5 empty] | Weight of Soil, Ws = | 107.1531 | kips | Ws = (Vs*ws)/1000 | [9 empty] | 0.75 | 8.4 | 5.2
| Weight of Ends of Tank, We = | 0.84653 | kips | We = Ae*(t/12)*w | [5 empty] | Thickness of Spread Foundation: | [12 empty] | 0.625 | 5.9 | 3.5
| Weight of Cylinder of Tank, Wc = | 2.804 | kips | Wc = Ac*(t/12)*w | [5 empty] | Req'd. Weight of Conc. Fdn., Wf = | 39.5622 | kips | Wf = (U(total)*FS)-(W(total)+Ws) >= 0 | [9 empty] | 0.5 | 3.8 | 2.2
| Total Weight of Tank, W(total) = | 4.6505 | kips | W(total) = Wc+We+Wm | [5 empty] | Buoyed Concrete Weight, wc = | 87.6 | pcf | wc = 150-62.4 (assume concrete unit wt. = 150 pcf) | [9 empty] | 0.375 | 2.1 | 1.2
[10 empty] | Req'd. Volume of Conc. Fdn., Vf = | 451.6234 | ft.^3 | Vf = Wf/(wc/1000)
Determine Uplift (Buoyant) Force: | [9 empty] | Req'd. Fdn. Thickness, Tf(req'd) = | 1.3 | ft. | Tf(req'd) = Vf/(Lf*Bf)
| Volume of Ends of Tank, Ve = | 263.9155 | ft.^3 | Ve = 2*(pi*(Le-t/12)*(3*OD^2+4*(Le-t/12)^2)/24) | [5 empty] | Anchor Strap Requirements: | [12 empty] | Anchor Strap (Gross) Allowable Load (kips)
| Volume of Cylinder of Tank, Vc = | 1332.0353 | ft.^3 | Vc = pi*ID^2/4*Lc | [5 empty] | Tension per Strap, Ts = | 12.0325 | kips | Ts = (U(total)-W(total))/(2*Na) | [9 empty] | Strap Thk. | Strap Width, bs (in.)
| Volume of Riser(s), Vr = | 21.2058 | ft.^3 | Vr = Nr*(pi*Dr^2/4*h) | [5 empty] | Allowable Tension Stress, Ft = | 21.6 | ksi | Ft = 0.60*Fy (Fy assumed = 36.0 ksi for strap) | [9 empty] | ts, (in.) | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6
| Total Volume of Tank, V(total) = | 1617.1566 | ft.^3 | V(total) = Vc+Ve+Vr | [5 empty] | Req'd. Tension Strap Thk., ts = | 0.18569 | in. | ts = Ts/(bs*Ft) | [9 empty] | 1 | 21.6 | 32.4 | 43.2 | 54 | 64.8 | 75.6 | 86.4 | 97.2 | 108 | 118.8 | 129.6
| Uplift Force on Tank Ends, Ue = | 16.4683 | kips | Ue = (62.4*Ve)/1000 | [5 empty] | Tension Strap Thk. Used, ts(used) = | 0.1875 | in. | [10 empty] | 0.9375 | 20.3 | 30.4 | 40.5 | 50.6 | 60.8 | 70.9 | 81 | 91.1 | 101.3 | 111.4 | 121.5
| Uplift Force on Cylinder of Tank, Uc = | 83.119 | kips | Uc = (62.4*Vc)/1000 | [5 empty] | Anchor Strap Allowable Load, Ta = | 12.2 | kips | Ta = (ts(used)*bs)*Ft | [9 empty] | 0.875 | 18.9 | 28.4 | 37.8 | 47.3 | 56.7 | 66.2 | 75.6 | 85.1 | 94.5 | 104 | 113.4
| Uplift Force on Risers, Ur = | 1.3232 | kips | Ur = (62.4*Vr)/1000 | [5 empty] | Anchor Rod Requirements: | [12 empty] | 0.8125 | 17.6 | 26.3 | 35.1 | 43.9 | 52.7 | 61.4 | 70.2 | 79 | 87.8 | 96.5 | 105.3
| Total Uplift Force on Tank, U(total) = | 100.9106 | kips | U(total) = Uc+Ue+Ur | [5 empty] | Tension per Anchor Rod, Tr = | 12.0325 | kips | Tr = (U(total)-W(total))/(2*Na) | [9 empty] | 0.75 | 16.2 | 24.3 | 32.4 | 40.5 | 48.6 | 56.7 | 64.8 | 72.9 | 81 | 89.1 | 97.2
[10 empty] | Allowable Tension Stress, Ft = | 19.1 | ksi | Ft = 0.33*Fu = 19.1 for A-36 threaded rod (assumed) | [9 empty] | 0.6875 | 14.9 | 22.3 | 29.7 | 37.1 | 44.6 | 52 | 59.4 | 66.8 | 74.3 | 81.7 | 89.1
Determine Weight of Soil Above Spread Foundation: | [9 empty] | Req'd. Size of Anchor Rod, D = | 0.8956 | in. | D = SQRT(4*Tr/(pi*Ft) | [9 empty] | 0.625 | 13.5 | 20.3 | 27 | 33.8 | 40.5 | 47.3 | 54 | 60.8 | 67.5 | 74.3 | 81
| Volume of Soil, Vs = | 2515.332 | ft.^3 | Vs = ((h+OD+1.0')*Lf*Bf)-V(total) | [5 empty] | Size of Anchor Rod Used, D(used) = | 1 | in. | [10 empty] | 0.5625 | 12.2 | 18.2 | 24.3 | 30.4 | 36.5 | 42.5 | 48.6 | 54.7 | 60.8 | 66.8 | 72.9
| Buoyed Soil Unit Weight, ws = | 42.6 | pcf | ws = we-62.4 (unit weight of water = 62.4 pcf) | [5 empty] | Anchor Rod Allowable Load, Ta = | 15 | kips | Ta = Ft*(pi*D(used)^2/4) >= Tr | [9 empty] | 0.5 | 10.8 | 16.2 | 21.6 | 27 | 32.4 | 37.8 | 43.2 | 48.6 | 54 | 59.4 | 64.8
| Weight of Soil, Ws = | 107.1531 | kips | Ws = (Vs*ws)/1000 | [5 empty] | Turnbuckle Requirements: |  |  | Note: if used, turnbuckles will control rod size. | [9 empty] | 0.4375 | 9.5 | 14.2 | 18.9 | 23.6 | 28.4 | 33.1 | 37.8 | 42.5 | 47.3 | 52 | 56.7
[6 empty] | (continued) |  |  |  | Tension per Anchor Rod, Tr = | 12.0325 | kips | Tr = (U-W)/(2*Na) | [9 empty] | 0.375 | 8.1 | 12.2 | 16.2 | 20.3 | 24.3 | 28.4 | 32.4 | 36.5 | 40.5 | 44.6 | 48.6
[10 empty] | Req'd. Size of Turnbuckle, D = | 1.25 | in. | D = from AISC 9th Edition Manual, page 4-149, for Ta >= Tr | [9 empty] | 0.3125 | 6.8 | 10.1 | 13.5 | 16.9 | 20.3 | 23.6 | 27 | 30.4 | 33.8 | 37.1 | 40.5
Determine Thickness of Spread Foundation: | [9 empty] | Turnbuckle Allowable Load, Ta = | 15.2 | kips | Ta >= Tr (from AISC 9th Edition Manual, page 4-149) | [9 empty] | 0.25 | 5.4 | 8.1 | 10.8 | 13.5 | 16.2 | 18.9 | 21.6 | 24.3 | 27 | 29.7 | 32.4
| Req'd. Weight of Conc. Fdn., Wf = | 39.5622 | kips | Wf = (U(total)*FS)-(W(total)+Ws) >= 0 | [5 empty] | Spread Foundation Reinforcing: |  |  | (for short direction) | [9 empty] | 0.1875 | 4.1 | 6.1 | 8.1 | 10.1 | 12.2 | 14.2 | 16.2 | 18.2 | 20.3 | 22.3 | 24.3
| Buoyed Concrete Weight, wc = | 87.6 | pcf | wc = 150-62.4 (assume concrete unit wt. = 150 pcf) | [5 empty] | Eff. Width per Strap/Anchor, be = | 5.3 | ft. | be = Lc/(Na+1) | [9 empty] | 0.125 | 2.7 | 4.1 | 5.4 | 6.8 | 8.1 | 9.5 | 10.8 | 12.2 | 13.5 | 14.9 | 16.2
| Req'd. Volume of Conc. Fdn., Vf = | 451.6234 | ft.^3 | Vf = Wf/(wc/1000) | [5 empty] | Max. Percent Flex. Reinf., r(max) = | 0.02138 |  | r(max) = 0.75*0.85*b1*f'c/fy*(87/(87+fy))
| Req'd. Fdn. Thickness, Tf(req'd) = | 1.3 | ft. | Tf(req'd) = Vf/(Lf*Bf) | [5 empty] | +Moment between Anchors, +Mu = | 4.6919 | ft.-kips/ft. | +Mu = 1.6*(2*Tr/(8*Bf)*((OD+6"/12)^2….
….-4*((Bf-(OD+6"/12))/2)^2)/be) (Average L.F. = 1.6)
Determine Anchor Strap Requirements: | [9 empty] | Effect. Depth for Bot. Reinf., d1 = | 14 | in. | d1 = Tf*12 - 4"
| Tension per Strap, Ts = | 12.0325 | kips | Ts = (U(total)-W(total))/(2*Na) | [5 empty] | Req'd. Percent Flexural Reinf., r1 = | 0.00044505 |  | r1 = (0.9*fy-((0.9*fy)^2-4*(0.9*0.59*fy^2/f'c)*….
| Allowable Tension Stress, Ft = | 21.6 | ksi | Ft = 0.60*Fy (Fy assumed = 36.0 ksi for strap) | [8 empty] | ….(12*Mu/(12*d1^2)))^(1/2))/(2*(0.9*0.59*fy^2/f'c))
| Req'd. Tension Strap Thk., ts = | 0.18569 | in. | ts = Ts/(bs*Ft) | [5 empty] | Req'd. Flexural Reinforcing, +As = | 0.074768 | in.^2/ft. | +As = r1*b*d1 (b = 12")
| Tension Strap Thk. Used, ts(used) = | 0.1875 | in. | [6 empty] | -Moment at Anchors, -Mu = | 1.7669 | ft.-kips/ft. | -Mu = 1.6*(2*Tr/Bf*((Bf-(OD+6"/12))/2)^2/be)
| Anchor Strap Allowable Load, Ta = | 12.2 | kips | Ta = (ts(used)*bs)*Ft | [5 empty] | Effect. Depth for Top Reinf., d2 = | 15 | in. | d2 = Tf*12 - 3"
[10 empty] | Req'd. Percent Flexural Reinf., r2 = | 0.00014561 |  | r2 = (0.9*fy-((0.9*fy)^2-4*(0.9*0.59*fy^2/f'c)*….
Determine Anchor Rod Requirements: | [12 empty] | ….(12*Mu/(12*d2^2)))^(1/2))/(2*(0.9*0.59*fy^2/f'c))
| Tension per Anchor Rod, Tr = | 12.0325 | kips | Tr = (U(total)-W(total))/(2*Na) | [5 empty] | Req'd. Flexural Reinforcing, -As = | 0.02621 | in.^2/ft. | -As = r2*b*d2 (b = 12")
| Allowable Tension Stress, Ft = | 19.1 | ksi | Ft = 0.33*Fu = 19.1 for A-36 threaded rod (assumed) | [5 empty] | Min. Temp. Reinf./Face, As(temp) = | 0.1944 | in.^2/ft. | As(temp) = (0.0018/2)*b*(Tf*12) (b = 12'')
| Req'd. Size of Anchor Rod, D = | 0.8956 | in. | D = SQRT(4*Tr/(pi*Ft)
| Size of Anchor Rod Used, D(used) = | 1 | in.
| Anchor Rod Allowable Load, Ta = | 15 | kips | Ta = Ft*(pi*D(used)^2/4) >= Tr |  |  |  | Anchor Rod Data |  |  | Turnbuckle Data
[8 empty] | Dia., D | Allowable |  | Dia., D | Safe Working
Determine Turnbuckle Requirements: |  |  |  | Note: if used, turnbuckles will control rod size. |  |  | Index # | (in.) | Load (kips) | Index # | (in.) | Load (kips)
| Tension per Anchor Rod, Tr = | 12.0325 | kips | Tr = (U-W)/(2*Na) |  |  | 1 | 5 | 375 | 1 | 5 | 294.7
| Req'd. Size of Rod/Turnbuckle, D = | 1.25 | in. |  |  |  | 2 | 4.75 | 338.5 | 2 | 4.75 | 233.8
| Turnbuckle Allowable Load, Ta = | 15.2 | kips | Ta >= Tr (from AISC 9th Edition Manual, page 4-149) |  |  | 3 | 4.5 | 303.8 | 3 | 4.5 | 233.8
[7 empty] | 4 | 4.25 | 271 | 4 | 4.25 | 233.8 | [10 empty] | 0.75: Reinforcing Bar Area for Various Bar Spacings (in.^2/ft.)
Determine Spread Foundation Reinforcing: |  |  |  | (for short direction) |  |  | 5 | 4 | 240 | 5 | 4 | 167.8 | [10 empty] | 0.75: Spacing; 16.2: Bar Size
| Eff. Width per Strap/Anchor, be = | 5.3 | ft. | be = Lc/(Na+1) |  |  | 6 | 3.75 | 211 | 6 | 3.75 | 167.8 | [10 empty] | (in.) | #3 | #4 | #5 | #6 | #7 | #8 | #9 | #10 | #11
| Max. Percent Flex. Reinf., r(max) = | 0.02138 |  | r(max) = 0.75*0.85*b1*f'c/fy*(87/(87+fy)) |  |  | 7 | 3.5 | 183.8 | 7 | 3.5 | 122.2 | [10 empty] | 3 | 0.44 | 0.8 | 1.24 | 1.76 | 2.4 | 3.16 | 4 | 5.08 | 6.24
| +Moment between Anchors, +Mu = | 4.6919 | ft.-kips/ft. | +Mu = 1.6*(2*Tr/(8*Bf)*((OD+6"/12)^2…. |  |  | 8 | 3.25 | 158.4 | 8 | 3.25 | 122.2 | [10 empty] | 3-1/2 | 0.37714 | 0.68571 | 1.0629 | 1.5086 | 2.0571 | 2.7086 | 3.4286 | 4.3543 | 5.3486
|  |  |  | ….-4*((Bf-(OD+6"/12))/2)^2)/be) (Average L.F. = 1.6) |  |  | 9 | 3 | 135 | 9 | 3 | 96.7 | [10 empty] | 4 | 0.33 | 0.6 | 0.93 | 1.32 | 1.8 | 2.37 | 3 | 3.81 | 4.68
| Effect. Depth for Bot. Reinf., d1 = | 14 | in. | d1 = Tf*12 - 4" |  |  | 10 | 2.75 | 113.4 | 10 | 2.75 | 75 | [10 empty] | 4-1/2 | 0.29333 | 0.53333 | 0.82667 | 1.1733 | 1.6 | 2.1067 | 2.6667 | 3.3867 | 4.16
| Req'd. Percent Flexural Reinf., r1 = | 0.00044505 |  | r1 = (0.9*fy-((0.9*fy)^2-4*(0.9*0.59*fy^2/f'c)*…. |  |  | 11 | 2.5 | 93.8 | 11 | 2.5 | 60 | [10 empty] | 5 | 0.264 | 0.48 | 0.744 | 1.056 | 1.44 | 1.896 | 2.4 | 3.048 | 3.744
|  |  |  | ….(12*Mu/(12*d1^2)))^(1/2))/(2*(0.9*0.59*fy^2/f'c)) |  |  | 12 | 2.25 | 75.9 | 12 | 2.25 | 48 | [10 empty] | 5-1/2 | 0.24 | 0.43636 | 0.67636 | 0.96 | 1.3091 | 1.7236 | 2.1818 | 2.7709 | 3.4036
| Req'd. Flexural Reinforcing, +As = | 0.074768 | in.^2/ft. | As1 = r1*b*d1 (b = 12") |  |  | 13 | 2 | 60 | 13 | 2 | 37.2 | [10 empty] | 6 | 0.22 | 0.4 | 0.62 | 0.88 | 1.2 | 1.58 | 2 | 2.54 | 3.12
| -Moment at Anchors, -Mu = | 1.7669 | ft.-kips/ft. | -Mu = 1.6*(2*Tr/Bf*((Bf-(OD+6"/12))/2)^2/be) |  |  | 14 | 1.875 | 52.7 | 14 | 1.875 | 37.2 | [10 empty] | 6-1/2 | 0.20308 | 0.36923 | 0.57231 | 0.81231 | 1.1077 | 1.4585 | 1.8462 | 2.3446 | 2.88
| Effect. Depth for Top Reinf., d2 = | 15 | in. | d2 = Tf*12 - 3" |  |  | 15 | 1.75 | 45.9 | 15 | 1.75 | 28.3 | [10 empty] | 7 | 0.18857 | 0.34286 | 0.53143 | 0.75429 | 1.0286 | 1.3543 | 1.7143 | 2.1771 | 2.6743
| Req'd. Percent Flexural Reinf., r2 = | 0.00014561 |  | r2 = (0.9*fy-((0.9*fy)^2-4*(0.9*0.59*fy^2/f'c)*…. |  |  | 16 | 1.625 | 39.6 | 16 | 1.625 | 24.5 | [10 empty] | 7-1/2 | 0.176 | 0.32 | 0.496 | 0.704 | 0.96 | 1.264 | 1.6 | 2.032 | 2.496
|  |  |  | ….(12*Mu/(12*d2^2)))^(1/2))/(2*(0.9*0.59*fy^2/f'c)) |  |  | 17 | 1.5 | 33.8 | 17 | 1.5 | 21 | [10 empty] | 8 | 0.165 | 0.3 | 0.465 | 0.66 | 0.9 | 1.185 | 1.5 | 1.905 | 2.34
| Req'd. Flexural Reinforcing, -As = | 0.02621 | in.^2/ft. | -As = r2*b*d2 (b = 12") |  |  | 18 | 1.375 | 28.4 | 18 | 1.375 | 17.4 | [10 empty] | 8-1/2 | 0.15529 | 0.28235 | 0.43765 | 0.62118 | 0.84706 | 1.1153 | 1.4118 | 1.7929 | 2.2024
| Min. Temp. Reinf./Face, As(temp) = | 0.1944 | in.^2/ft. | As(temp) = (0.0018/2)*b*(Tf*12) (b = 12'') |  |  | 19 | 1.25 | 23.4 | 19 | 1.25 | 15.2 | [10 empty] | 9 | 0.14667 | 0.26667 | 0.41333 | 0.58667 | 0.8 | 1.0533 | 1.3333 | 1.6933 | 2.08
[7 empty] | 20 | 1.125 | 19 | 20 | 1.125 | 11.6 | [10 empty] | 9-1/2 | 0.13895 | 0.25263 | 0.39158 | 0.55579 | 0.75789 | 0.99789 | 1.2632 | 1.6042 | 1.9705
[7 empty] | 21 | 1 | 15 | 21 | 1 | 9.3 | [10 empty] | 10 | 0.132 | 0.24 | 0.372 | 0.528 | 0.72 | 0.948 | 1.2 | 1.524 | 1.872
Comments: | [6 empty] | 22 | 0.875 | 11.5 | 22 | 0.875 | 7.2 | [10 empty] | 10-1/2 | 0.12571 | 0.22857 | 0.35429 | 0.50286 | 0.68571 | 0.90286 | 1.1429 | 1.4514 | 1.7829
[7 empty] | 23 | 0.75 | 8.4 | 23 | 0.75 | 5.2 | [10 empty] | 11 | 0.12 | 0.21818 | 0.33818 | 0.48 | 0.65455 | 0.86182 | 1.0909 | 1.3855 | 1.7018
[7 empty] | 24 | 0.625 | 5.9 | 24 | 0.625 | 3.5 | [10 empty] | 11-1/2 | 0.11478 | 0.2087 | 0.32348 | 0.45913 | 0.62609 | 0.82435 | 1.0435 | 1.3252 | 1.6278
[7 empty] | 25 | 0.5 | 3.8 | 25 | 0.5 | 2.2 | [10 empty] | 12 | 0.11 | 0.2 | 0.31 | 0.44 | 0.6 | 0.79 | 1 | 1.27 | 1.56
[7 empty] | 26 | 0.375 | 2.1 | 26 | 0.375 | 1.2
Anchor Strap (Gross) Allowable Loads (kips)
[8 empty] | Strap Thk. | Strap Width, bs (in.)
[7 empty] | Index # | ts, (in.) | 1 | 1.5 | 2 | 2.5 | 3 | 3.5 | 4 | 4.5 | 5 | 5.5 | 6 | Index # | 3
[7 empty] | 1 | 1 | 21.6 | 32.4 | 43.2 | 54 | 64.8 | 75.6 | 86.4 | 97.2 | 108 | 118.8 | 129.6 | 1 | 64.8
[7 empty] | 2 | 0.9375 | 20.3 | 30.4 | 40.5 | 50.6 | 60.8 | 70.9 | 81 | 91.1 | 101.3 | 111.4 | 121.5 | 2 | 60.8
[7 empty] | 3 | 0.875 | 18.9 | 28.4 | 37.8 | 47.3 | 56.7 | 66.2 | 75.6 | 85.1 | 94.5 | 104 | 113.4 | 3 | 56.7
[7 empty] | 4 | 0.8125 | 17.6 | 26.3 | 35.1 | 43.9 | 52.7 | 61.4 | 70.2 | 79 | 87.8 | 96.5 | 105.3 | 4 | 52.7
[7 empty] | 5 | 0.75 | 16.2 | 24.3 | 32.4 | 40.5 | 48.6 | 56.7 | 64.8 | 72.9 | 81 | 89.1 | 97.2 | 5 | 48.6
[7 empty] | 6 | 0.6875 | 14.9 | 22.3 | 29.7 | 37.1 | 44.6 | 52 | 59.4 | 66.8 | 74.3 | 81.7 | 89.1 | 6 | 44.6
[7 empty] | 7 | 0.625 | 13.5 | 20.3 | 27 | 33.8 | 40.5 | 47.3 | 54 | 60.8 | 67.5 | 74.3 | 81 | 7 | 40.5
[7 empty] | 8 | 0.5625 | 12.2 | 18.2 | 24.3 | 30.4 | 36.5 | 42.5 | 48.6 | 54.7 | 60.8 | 66.8 | 72.9 | 8 | 36.5
[7 empty] | 9 | 0.5 | 10.8 | 16.2 | 21.6 | 27 | 32.4 | 37.8 | 43.2 | 48.6 | 54 | 59.4 | 64.8 | 9 | 32.4
[7 empty] | 10 | 0.4375 | 9.5 | 14.2 | 18.9 | 23.6 | 28.4 | 33.1 | 37.8 | 42.5 | 47.3 | 52 | 56.7 | 10 | 28.4
[7 empty] | 11 | 0.375 | 8.1 | 12.2 | 16.2 | 20.3 | 24.3 | 28.4 | 32.4 | 36.5 | 40.5 | 44.6 | 48.6 | 11 | 24.3
[7 empty] | 12 | 0.3125 | 6.8 | 10.1 | 13.5 | 16.9 | 20.3 | 23.6 | 27 | 30.4 | 33.8 | 37.1 | 40.5 | 12 | 20.3
[7 empty] | 13 | 0.25 | 5.4 | 8.1 | 10.8 | 13.5 | 16.2 | 18.9 | 21.6 | 24.3 | 27 | 29.7 | 32.4 | 13 | 16.2
[7 empty] | 14 | 0.1875 | 4.1 | 6.1 | 8.1 | 10.1 | 12.2 | 14.2 | 16.2 | 18.2 | 20.3 | 22.3 | 24.3 | 14 | 12.2
[7 empty] | 15 | 0.125 | 2.7 | 4.1 | 5.4 | 6.8 | 8.1 | 9.5 | 10.8 | 12.2 | 13.5 | 14.9 | 16.2 | 15 | 8.1
Note on AC10: Values shown for allowable load for anchor rods are calculated as follows: T = p*D^2/4*Ft where: Ft = 0.33*Fu = 19.1 ksi Fu = 58.0 ksi
Note on AD10: Values shown for safe working load for turnbuckles are from AISC 9th Edition Manual (ASD) page 4-149, and are based on a 5:1 safety factor.
Note on D85: The ultimate "positive" moment for bottom reinforcing, +Mu, between the ends of a strap or rod anchor is determined assuming an effective strip of the foundation in the short direction an treating it as a simply supported beam with cantilevers (overhangs) at each end. The ends of the anchor serve as the supports. The assumed uniform loading on this "beam strip" is determined as: w = 2*Tr/Bf. Note: the positive moment formula for a uniformly loaded simply suported beam with overhangs at each end is: +M = w/8*(L^2-4*a^2) where: w = uniform load L = span btween supports a = length of cantilevers (overhangs)
Note on D91: The ultimate "negative" moment for top reinforcing, -Mu, at the ends of a strap or rod anchor is determined assuming an effective strip of the foundation in the short direction an treating it as a simply supported beam with overhangs at each end. The ends of the anchor serve as the supports. The assumed uniform loading on this "beam strip" is determined as: w = 2*Tr/Bf. Note: the negative moment formula for a uniformly loaded simply suported beam with overhangs at each end is: -M = w*a^2/2 where: w = uniform load L = span between supports a = length of cantilevers (overhangs)
Note on X106: Values shown for allowable capacities for anchor straps are calculated as follows based on the strap gross cross sectional area: T(allow) = (ts*bs)*Ft where: Ft = 0.6*Fy Fy = 36.0 ksi
Note on AM42: Values shown for allowable capacities for anchor straps are calculated as follows based on the strap gross cross sectional area: T(allow) = (ts*bs)*Ft where: Ft = 0.6*Fy Fy = 36.0 ksi
Note on AA1: "UGTANK.xls" written by: Alex Tomanovich, P.E.
Straps
Lf
Bf
OD+6"
ID
Lc
h
Tf
OD
Le
Le
W.T.
Grade
or Rods
Riser
1' thk. sand bed
be