## Doc
"FMG128" --- FACTORY MUTUAL GLOBAL WIND UPLIFT RATINGS
Program Description:
"FMG128" is a spreadsheet program written in MS-Excel for the purpose of determining Factory Mutual Global
(FMG) required roof zone ratings for the three (3) zones of a roof, based on FMG Data Sheet 1-28 (2009/2011).
This program is a workbook consisting of two (2) worksheets, described as follows:
Worksheet Name | Description
Doc | This documentation sheet
FMG Roof Uplift Ratings | Roof Wind Uplift Pressure Ratings per Factory Mutual Global 1-28
Program Assumptions and Limitations:
1. This program is based on the following reference:
Data Sheet 1-28: "Wind Design" - by Factory Mutual Global, 2009 (Revised April 2011)
2. In the "FMG Roof Uplift Ratings" worksheet, the FMG roof Zone 1 (Field Area) Rating is determined as follows:
a. Get Field Area design pressure from either Table 3, 4, or 5 depending on the Exposure, either B, C, or D.
b. Apply multiplier for Zone 1 from Table 6.
c. Apply a Factor of Safety multiplier of 2.
d. Round value up to the next highest 15 psf rating interval to arrive at the FMG Zone 1 (Field Area) Rating.
Note: for Zone 2 (Perimeter) and Zone 3 (Corners)
3. In the "FMG Roof Uplift Ratings" worksheet, the FMG roof Zone 2 (Perimeter) Rating is determined as follows:
a. Get Field Area design pressure from either Table 3, 4, or 5 depending on the Exposure, either B, C, or D.
b. Apply multiplier for Zone 2 from Table 6.
c. Apply a Factor of Safety multiplier of 2.
d. Round value up to the next highest 15 psf rating interval to arrive at the FMG Zone 2 (Perimeter) Rating.
4. In the "FMG Roof Uplift Ratings" worksheet, the FMG roof Zone 3 (Corners) Rating is determined as follows:
a. Get Field Area design pressure from either Table 3, 4, or 5 depending on the Exposure, either B, C, or D.
b. Apply multiplier for Zone 3 from Table 6.
c. Apply a Factor of Safety multiplier of 2.
d. Round value up to the next highest 15 psf rating interval to arrive at the FMG Zone 3 (Corners) Rating.
5. For components and cladding (roof deck, fasteners, and above deck components), FMG 1-28 requires that
the effective area be set = 10 ft.^2 along with an Importance Factor = 1.15.
For secondary supporting members (purlins or joists) per FMG 1-28 Section 2.2.3, refer to applicable
ASCE 7 Standard and apply the appropriate effective tributary area along with an Importance Factor = 1.15.
6. This program contains numerous “comment boxes” which contain a wide variety of information including
explanations of input or output items, equations used, data tables, etc. (Note: presence of a “comment box”
is denoted by a “red triangle” in the upper right-hand corner of a cell. Merely move the mouse pointer to the
desired cell to view the contents of that particular "comment box".)

## FMG Roof Uplift Ratings
ROOF WIND UPLIFT PRESSURE RATINGS | [21 empty] | Version 1.1
Per Factory Mutual Global (FMG) Data Sheet 1-28: "Wind Design" (2009/2011) | [23 empty] | From: FM Global - Property Loss Prevention Data Sheets 1-28, Wind Design (2009/2011)
for Roof Deck Securement and Above-Deck Roof Components | [7 empty] | Enclosed
Job Name: |  |  |  |  | Subject: |  |  | Part. Encl.
Job Number: |  |  |  |  | Originator: |  | Checker: | B
C
Input Data: | [7 empty] | D
Gable
| Basic Wind Speed, V = | 90 | mph |  |  |  |  | Monoslope
| Enclosed or Part. Encl. = | Enclosed
| Exposure Category = | C
| Ridge Height, hr = | 62.083 | ft. (hr >= he)
| Eave Height, he = | 60 | ft. (he <= hr) | [5 empty] | Calculations:
| Building Dimension, L = | 100 | ft.
| Building Dimension, B = | 200 | ft. | [5 empty] | FMG DS 1-28 - Table 3 (Exposure B)
| Roof Type = | Gable | [5 empty] | Index | h | 85 | 90 | 100 | 110 | 120 | 130 | 140 | 145 | 150 | 160 | 170 | 185
[8 empty] | 1 | 0 | 15 | 17 | 21 | 25 | 30 | 35 | 41 | 43 | 47 | 53 | 60 | 71
[8 empty] | 2 | 15 | 15 | 17 | 21 | 25 | 30 | 35 | 41 | 43 | 47 | 53 | 60 | 71
Results: | [7 empty] | 3 | 30 | 15 | 17 | 21 | 25 | 30 | 35 | 41 | 43 | 47 | 53 | 60 | 71
[8 empty] | 4 | 60 | 18 | 20 | 25 | 31 | 36 | 43 | 49 | 53 | 57 | 65 | 73 | 86
Parameters and Coefficients: | [7 empty] | 5 | 89 | 20 | 23 | 28 | 34 | 41 | 48 | 55 | 60 | 64 | 72 | 82 | 97
| Roof Angle, q = | 2.3856 | deg. |  |  |  |  | 6 | 90 | 27 | 31 | 38 | 46 | 55 | 64 | 74 | 80 | 86 | 97 | 110 | 130
| Mean Roof Ht., h = | 60 | ft. | h = he, for roof angle <=10 deg. |  |  |  | 7 | 100 | 28 | 32 | 39 | 47 | 56 | 66 | 77 | 82 | 88 | 100 | 113 | 134
| w = | 100 | ft. | w = Lesser of L or B building dimension |  |  |  | 8 | 200 | 34 | 39 | 48 | 58 | 69 | 80 | 93 | 100 | 107 | 122 | 138 | 163
| h/w = | 0.6 |  | Ratio of mean roof ht. to least bldg. dimension (for Table 6) |  |  |  | 9 | 300 | 39 | 43 | 53 | 65 | 77 | 91 | 105 | 112 | 121 | 137 | 155 | 183
| Importance Factor, I = | 1.15 |  | I = 1.15, per FMG 1-28, Section 2.2(a) |  |  |  | 10 | 400 | 42 | 47 | 58 | 70 | 84 | 98 | 114 | 122 | 131 | 149 | 168 | 199
| Effective Area, Ae = | 10 | ft.^2 | Ae <= 10 ft.^2, as limited by FMG 1-28, Section 2.2(d) |  |  |  | 11 | 500 | 45 | 50 | 62 | 75 | 89 | 105 | 121 | 130 | 139 | 158 | 179 | 212
| Zone 2 Dimension, a = | 10 | ft. | a = max. of (min. of (0.1*w or 0.4*h), 0.04*w or 3')
| Zone 3 Dimension, a = | 10 | ft. | a = max. of (min. of (0.1*w or 0.4*h), 0.04*w or 3') |  |  |  |  | Interpolating:
[8 empty] | 4 | 60 | 18 | 20 | 25 | 31 | 36 | 43 | 49 | 53 | 57 | 65 | 73 | 86
Zone 1 (Roof Field Area) Uplift Design Pressure and Rating: | [8 empty] | 60 | 18 | 20 | 25 | 31 | 36 | 43 | 49 | 53 | 57 | 65 | 73 | 86
|  |  | Zone 1 (Field Area) Basic Uplift Pressure, pb1 = | 27 | psf | pb1 = from FMG 1-28, Table 4 |  | 5 | 89 | 20 | 23 | 28 | 34 | 41 | 48 | 55 | 60 | 64 | 72 | 82 | 97
|  |  | Zone 1 Negative Pressure Multiplier, C1 = | 1 |  | C1 = from FMG 1-28, Table 6 |  |  | Result:
|  |  | Zone 1 (Field Area) Design Uplift Pressure, pd1 = | 27 | psf | pd1 = pb1*C1 |  | 90 | 20 | psf
|  |  | FMG Factor of Safety, FS = | 2 |  | FS = 2, per FMG 1-28 | [15 empty] | Zone 1 Rating
|  |  | FMG Zone 1 (Field Area) Pressure, p1 = | 54 | psf | p1 = pd1*FS | [15 empty] | from Table 8:
|  |  | Zone 1 FMG Rating = | 1-60 |  | p1 rounded up to next 15 psf interval |  |  | FMG DS 1-28 - Table 4 (Exposure C) | [12 empty] | 1-60
[8 empty] | Index | h | 85 | 90 | 100 | 110 | 120 | 130 | 140 | 145 | 150 | 160 | 170 | 185
Zone 2 (Perimeter Area) Uplift Design Pressure and Rating: | [7 empty] | 1 | 0 | 18 | 20 | 25 | 31 | 36 | 42 | 49 | 53 | 56 | 64 | 73 | 86
|  |  | Zone 1 (Field Area) Basic Uplift Pressure, pb1 = | 27 |  | pb1 = from FMG 1-28, Table 4 |  | 2 | 15 | 18 | 20 | 25 | 31 | 36 | 42 | 49 | 53 | 56 | 64 | 73 | 86
|  |  | Zone 2 Negative Pressure Multiplier, C2 = | 1.68 |  | C2 = from FMG 1-28, Table 6 |  | 3 | 30 | 21 | 23 | 29 | 35 | 42 | 49 | 57 | 61 | 65 | 74 | 84 | 99
|  |  | Zone 2 (Perimeter) Design Uplift Pressure, pd2 = | 45.36 | psf | pd2 = pb1*C2 |  | 4 | 60 | 24 | 27 | 34 | 41 | 48 | 57 | 66 | 71 | 76 | 86 | 97 | 115
|  |  | FMG Factor of Safety, FS = | 2 |  | FS = 2, per FMG 1-28 |  | 5 | 89 | 26 | 30 | 37 | 44 | 53 | 62 | 72 | 77 | 82 | 94 | 106 | 125 | Zone 2 Rating
|  |  | FMG Zone 2 (Perimeter Area) Pressure, p2 = | 90.72 | psf | p2 = pd2*FS |  | 6 | 90 | 35 | 40 | 49 | 59 | 70 | 83 | 96 | 103 | 110 | 125 | 141 | 168 | from Table 8:
|  |  | Zone 2 FMG Rating = | 1-105 |  | p2 rounded up to next 15 psf interval |  | 7 | 100 | 36 | 41 | 50 | 61 | 72 | 85 | 98 | 105 | 113 | 128 | 145 | 171 | 1-105
[8 empty] | 8 | 200 | 42 | 47 | 59 | 70 | 83 | 98 | 113 | 122 | 130 | 148 | 167 | 198
Zone 3 (Corner Area) Uplift Design Pressure and Rating: | [7 empty] | 9 | 300 | 46 | 51 | 63 | 76 | 91 | 107 | 124 | 133 | 142 | 161 | 182 | 216
|  |  | Zone 1 (Field Area) Basic Uplift Pressure, pb1 = | 27 | psf | pb1 = from FMG 1-28, Table 4 |  | 10 | 400 | 48 | 54 | 67 | 81 | 96 | 113 | 131 | 141 | 151 | 172 | 194 | 229
|  |  | Zone 3 Negative Pressure Multiplier, C3 = | 2.53 |  | C3 = from FMG 1-28, Table 6 |  | 11 | 500 | 51 | 57 | 70 | 85 | 101 | 119 | 138 | 148 | 158 | 180 | 203 | 240
|  |  | Zone 3 (Corner) Design Uplift Pressure, pd3 = | 68.31 | psf | pd3 = pb1*C3
|  |  | FMG Factor of Safety, FS = | 2 |  | FS = 2, per FMG 1-28 |  |  | Interpolating: | [12 empty] | Zone 3 Rating
|  |  | FMG Zone 3 (Corner Area) Pressure, p3 = | 136.62 | psf | p3 = pd3*FS |  | 4 | 60 | 24 | 27 | 34 | 41 | 48 | 57 | 66 | 71 | 76 | 86 | 97 | 115 | from Table 8:
|  |  | Zone 3 FMG Rating = | 1-150 |  | p3 rounded up to next 15 psf interval |  |  | 60 | 24 | 27 | 34 | 41 | 48 | 57 | 66 | 71 | 76 | 86 | 97 | 115 | 1-150
[8 empty] | 5 | 89 | 26 | 30 | 37 | 44 | 53 | 62 | 72 | 77 | 82 | 94 | 106 | 125
Result:
[8 empty] | 90 | 27 | psf
FMG DS 1-28 - Table 5 (Exposure D)
[8 empty] | Index | h | 85 | 90 | 100 | 110 | 120 | 130 | 140 | 145 | 150 | 160 | 170 | 185
[8 empty] | 1 | 0 | 22 | 25 | 31 | 37 | 44 | 51 | 60 | 64 | 68 | 78 | 88 | 104
[8 empty] | 2 | 15 | 22 | 25 | 31 | 37 | 44 | 51 | 60 | 64 | 68 | 78 | 88 | 104
[8 empty] | 3 | 30 | 25 | 28 | 34 | 42 | 49 | 58 | 67 | 72 | 77 | 88 | 99 | 117
[8 empty] | 4 | 60 | 28 | 31 | 39 | 47 | 56 | 65 | 76 | 81 | 87 | 99 | 112 | 133
[8 empty] | 5 | 89 | 30 | 34 | 42 | 50 | 60 | 70 | 81 | 87 | 93 | 106 | 120 | 142
[8 empty] | 6 | 90 | 40 | 45 | 56 | 67 | 80 | 94 | 109 | 117 | 125 | 142 | 161 | 190
[8 empty] | 7 | 100 | 41 | 46 | 57 | 69 | 82 | 96 | 111 | 119 | 127 | 145 | 164 | 194
[8 empty] | 8 | 200 | 46 | 52 | 64 | 77 | 92 | 108 | 125 | 134 | 144 | 164 | 185 | 219
[8 empty] | 9 | 300 | 50 | 56 | 69 | 83 | 99 | 117 | 134 | 144 | 154 | 176 | 198 | 235
[8 empty] | 10 | 400 | 52 | 58 | 72 | 87 | 104 | 122 | 141 | 152 | 162 | 185 | 208 | 247
[8 empty] | 11 | 500 | 54 | 61 | 75 | 91 | 108 | 127 | 147 | 158 | 169 | 192 | 217 | 257
Interpolating:
[8 empty] | 4 | 60 | 28 | 31 | 39 | 47 | 56 | 65 | 76 | 81 | 87 | 99 | 112 | 133
[9 empty] | 60 | 28 | 31 | 39 | 47 | 56 | 65 | 76 | 81 | 87 | 99 | 112 | 133
[8 empty] | 5 | 89 | 30 | 34 | 42 | 50 | 60 | 70 | 81 | 87 | 93 | 106 | 120 | 142
Result:
[8 empty] | 90 | 31 | psf
FMG DS 1-28 - Table 6 (No interpolating for roof angle)
[9 empty] | h | Roof | Enclosed Building |  |  | Part. Enclosed Bldg.
[8 empty] | Index | (ft.) | Angle, f | Zone 1 | Zone 2 | Zone 3 | Zone 1 | Zone 2 | Zone 3
[8 empty] | 1 | h<=60 | 0 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
[8 empty] | 2 | and | 7 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
[8 empty] | 3 | h/w<=1, | 27 | 0.92 | 1.59 | 2.36 | 1.23 | 1.91 | 2.67
[8 empty] | 4 | 60<h<90 | 45 | 1 | 1.17 | 1.17 | 1.31 | 1.48 | 1.48
[8 empty] | 5 |  | 0 | 1.34 | 2.1 | 2.86 | 1.65 | 2.42 | 3.18
[8 empty] | 6 | h/w>1, | 10 | 1.34 | 2.1 | 2.86 | 1.65 | 2.42 | 3.18
[8 empty] | 7 | 60<h<90 | 27 | 0.92 | 1.59 | 2.36 | 1.23 | 1.91 | 2.67
[8 empty] | 8 |  | 45 | 1 | 1.17 | 1.17 | 1.31 | 1.48 | 1.48
[8 empty] | 9 |  | 0 | 1 | 1.57 | 2.14 | 1.23 | 1.8 | 2.37
[8 empty] | 10 | h>=90 | 10 | 1 | 1.57 | 2.14 | 1.23 | 1.8 | 2.37
[8 empty] | 11 |  | 27 | 0.68 | 1.19 | 1.76 | 0.92 | 1.42 | 1.99
[8 empty] | 12 |  | 45 | 0.75 | 0.87 | 0.87 | 0.98 | 1.11 | 1.11
Case 1: Interpolating for h <= 60 and when h/w <= 1 for 60 < h < 90
[10 empty] | 2.3856 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
Case 2: Interpolating for h/w > 1 for 60 < h < 90
[10 empty] | 2.3856 | 1.34 | 2.1 | 2.86 | 1.65 | 2.42 | 3.18
Case 3: Interpolating for h >= 90
[10 empty] | 2.3856 | 1 | 1.57 | 2.14 | 1.23 | 1.8 | 2.37
[9 empty] | Case 1: | 2.3856 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
[9 empty] | Case 2: | 2.3856 | N.A. | N.A. | N.A. | N.A. | N.A. | N.A.
[9 empty] | Case 3: | 2.3856 | N.A. | N.A. | N.A. | N.A. | N.A. | N.A.
[9 empty] | Results: |  | Zone 1 | Zone 2 | Zone 3 | Zone 1 | Zone 2 | Zone 3
[11 empty] | 1 | 1.68 | 2.53 | N.A. | N.A. | N.A.
[8 empty] | (Note: NOT USED) | FMG DS 1-28 - Table 6 (Interpolating for the roof angle)
[9 empty] | h | Roof | Zone 1: Enclosed Building; Zone 1: Part. Enclosed Bldg.
[8 empty] | Index | (ft.) | Angle, f | Zone 1 | Zone 2 | Zone 3 | Zone 1 | Zone 2 | Zone 3
[8 empty] | 1 | h<=60 | 0 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
[8 empty] | 2 | and | 7 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
[8 empty] | 3 | h/w<=1, | 27 | 0.92 | 1.59 | 2.36 | 1.23 | 1.91 | 2.67
[8 empty] | 4 | 60<h<90 | 45 | 1 | 1.17 | 1.17 | 1.31 | 1.48 | 1.48
[8 empty] | 5 |  | 0 | 1.34 | 2.1 | 2.86 | 1.65 | 2.42 | 3.18
[8 empty] | 6 | h/w>1, | 10 | 1.34 | 2.1 | 2.86 | 1.65 | 2.42 | 3.18
[8 empty] | 7 | 60<h<90 | 27 | 0.92 | 1.59 | 2.36 | 1.23 | 1.91 | 2.67
[8 empty] | 8 |  | 45 | 1 | 1.17 | 1.17 | 1.31 | 1.48 | 1.48
[8 empty] | 9 |  | 0 | 1 | 1.57 | 2.14 | 1.23 | 1.8 | 2.37
[8 empty] | 10 | h>=90 | 10 | 1 | 1.57 | 2.14 | 1.23 | 1.8 | 2.37
[8 empty] | 11 |  | 27 | 0.68 | 1.19 | 1.76 | 0.92 | 1.42 | 1.99
[8 empty] | 12 |  | 45 | 0.75 | 0.87 | 0.87 | 0.98 | 1.11 | 1.11
Case 1: Interpolating for h <= 60 and when h/w <= 1 for 60 < h < 90
[9 empty] | 1 | 0 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
[10 empty] | 2.3856 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
[9 empty] | 2 | 7 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
Case 2: Interpolating for h/w > 1 for 60 < h < 90
[9 empty] | 5 | 0 | 1.34 | 2.1 | 2.86 | 1.65 | 2.42 | 3.18
[10 empty] | 2.3856 | 1.34 | 2.1 | 2.86 | 1.65 | 2.42 | 3.18
[9 empty] | 6 | 10 | 1.34 | 2.1 | 2.86 | 1.65 | 2.42 | 3.18
Case 3: Interpolating for h >= 90
[9 empty] | 9 | 0 | 1 | 1.57 | 2.14 | 1.23 | 1.8 | 2.37
[10 empty] | 2.3856 | 1 | 1.57 | 2.14 | 1.23 | 1.8 | 2.37
[9 empty] | 10 | 10 | 1 | 1.57 | 2.14 | 1.23 | 1.8 | 2.37
[9 empty] | Case 1: | 2.3856 | 1 | 1.68 | 2.53 | 1.31 | 1.99 | 2.85
[9 empty] | Case 2: | 2.3856 | N.A. | N.A. | N.A. | N.A. | N.A. | N.A.
[9 empty] | Case 3: | 2.3856 | N.A. | N.A. | N.A. | N.A. | N.A. | N.A.
[9 empty] | Results: |  | Zone 1 | Zone 2 | Zone 3 | Zone 1 | Zone 2 | Zone 3
[11 empty] | 1 | 1.68 | 2.53 | N.A. | N.A. | N.A.
FMG DS 1-28 - Table 8
(for enclosed bldgs., q <= 7, and h <= 60 ft.)
[9 empty] | Field | FMG DS 1-28 Wind Uplift Rating
[9 empty] | Press., p | Field | Zone 1: Perimeter; Zone 2: Corner
[9 empty] | 0 | 60 | Zone 1: 75; Zone 2: 105
[9 empty] | 15 | 60 | Zone 1: 75; Zone 2: 105
[9 empty] | 15.01 | 60 | Zone 1: 75; Zone 2: 105
[9 empty] | 20 | 60 | Zone 1: 75; Zone 2: 105
[9 empty] | 20.01 | 60 | Zone 1: 90; Zone 2: 120
[9 empty] | 25 | 60 | Zone 1: 90; Zone 2: 120
[9 empty] | 25.01 | 60 | Zone 1: 105; Zone 2: 150
[9 empty] | 30 | 60 | Zone 1: 105; Zone 2: 150
[9 empty] | 30.01 | 75 | Zone 1: 120; Zone 2: 180
[9 empty] | 37.5 | 75 | Zone 1: 120; Zone 2: 180
[9 empty] | 37.51 | 90 | Zone 1: 150; Zone 2: 225
[9 empty] | 45 | 90 | Zone 1: 150; Zone 2: 225
[9 empty] | 45.01 | 105 | Zone 1: 180; Zone 2: 270
[9 empty] | 52.5 | 105 | Zone 1: 180; Zone 2: 270
[9 empty] | 52.51 | 120 | Zone 1: 195; Zone 2: 300
[9 empty] | 60 | 120 | Zone 1: 195; Zone 2: 300
[9 empty] | 60.01 | 135 | Zone 1: 225; Zone 2: 330
[9 empty] | 67.5 | 135 | Zone 1: 225; Zone 2: 330
[9 empty] | 67.51 | 150 | Zone 1: 255; Zone 2: 360
[9 empty] | 75 | 150 | Zone 1: 255; Zone 2: 360
[9 empty] | 75.01 | 165 | Zone 1: 270; Zone 2: 405
[9 empty] | 82.5 | 165 | Zone 1: 270; Zone 2: 405
[9 empty] | 82.51 | 180 | Zone 1: 300; Zone 2: 435
[9 empty] | 90 | 180 | Zone 1: 300; Zone 2: 435
[9 empty] | 90.01 | 195 | Zone 1: 315; Zone 2: 480
[9 empty] | 97.5 | 195 | Zone 1: 315; Zone 2: 480
[9 empty] | 97.51 | 210 | Zone 1: 345; Zone 2: 510
[9 empty] | 105 | 210 | Zone 1: 345; Zone 2: 510
[9 empty] | 105.01 | 225 | Zone 1: 360; Zone 2: 540
[9 empty] | 112.5 | 225 | Zone 1: 360; Zone 2: 540
[9 empty] | 112.51 | 240 | Zone 1: 390; Zone 2: 585
[9 empty] | 120 | 240 | Zone 1: 390; Zone 2: 585
[9 empty] | 120.01 | 255 | Zone 1: 420; Zone 2: 615
[9 empty] | 127.5 | 255 | Zone 1: 420; Zone 2: 615
[9 empty] | 127.51 | 270 | Zone 1: 435; Zone 2: 660
[9 empty] | 135 | 270 | Zone 1: 435; Zone 2: 660
Results:
[9 empty] | Zone 1 = | 1-60 | Zone 1: FMG Rating
[9 empty] | Zone 2 = | 1-105 | Zone 1: FMG Rating
[9 empty] | Zone 3 = | 1-150 | Zone 1: FMG Rating | [6 empty] | Note!
Note on C13: The eave height, 'he', is the distance from the ground surface adjacent to the building to the roof eave line at a particular wall. If the height of the eave varies along the wall, the average height shall be used.
Note on C28: For h <= 60', width 'a' for Zone 2 is equal to 10% of least horizontal dimension or 0.4*h, whichever is smaller, but not less than either 4% of least horizontal dimension or 3'. For h > 60', width 'a' for Zone 2 is equal to 10% of least horizontal dimension, but not less than 3'.
Note on E37: Zone 1 FMG Rating = p1 pressure rounded up to the next highest 15 psf rating interval. Note: Use Zone 2 for Zone 1 for Gable roof when Ө > 7 deg. Rating 1-60 is the minimum FMG Rating.
Note on E45: Zone 2 FMG Rating = p2 pressure rounded up to the next highest 15 psf rating interval. Note: Use Zone 3 for Zone 2 for Gable roof when Ө <= 7 deg. and h > 60 ft. Use Zone 3 for Zone 2 for Gable roof when Ө > 7 deg. and h <= 60 ft.
Note on E53: Zone 3 FMG Rating = p3 pressure rounded up to the next highest 15 psf rating interval.
Note on E32: Note: FMG stipulates that interpolation is appropriate in use of Tables 3, 4, and 5.
Note on E33: Note: FMG does not stipulate that interpolation is appropriate in use of Table 6. Thus, interpolation is NOT used in Table 6 in detemining C1.
Note on E40: Note: FMG stipulates that interpolation is appropriate in use of Tables 3, 4, and 5.
Note on E41: Note: FMG does not stipulate that interpolation is appropriate in use of Table 6. Thus, interpolation is NOT used in Table 6 in detemining C2.
Note on E48: Note: FMG stipulates that interpolation is appropriate in use of Tables 3, 4, and 5.
Note on E49: Note: FMG does not stipulate that interpolation is appropriate in use of Table 6. Thus, interpolation is NOT used in Table 6 in detemining C3.
Note on C16: This program assumes that a Gable roof is symmetrical, as the ridge line is assumed in the center of the building dimension, 'L'. For flat roofs (roof angle = 0 degrees), either Gable or Monoslope may be used.
Note on C14: 'L' is the building dimension perpendicular to the building ridge.
Note on C15: 'B' is the building dimension parallel to the building ridge.
Note on AA1: "FMG128.xls" written by: Alex Tomanovich, P.E.
Nomenclature
Case 1:
Case 2:
Case 3:
Case 1:
Case 2:
Case 3: