## Doc
"MONORAIL" --- MONORAIL BEAM ANALYSIS
Program Description:
"MONORAIL" is a spreadsheet program written in MS-Excel for the purpose of analysis of either S-shape or
W-shape underhung monorail beams analyzed as simple-spans with or without overhangs (cantilevers).
Specifically, the x-axis and y-axis bending moments as well as any torsion effects are calculated. The actual and
allowable stresses are determined, and the effect of lower flange bending is also addressed by two different
approaches.
This program is a workbook consisting of three (3) worksheets, described as follows:
Worksheet Name |  | Description
Doc |  | This documentation sheet
S-shaped Monorail Beam |  | Monorail beam analysis for S-shaped beams
W-shaped Monorail Beam |  | Monorail beam analysis for W-shaped beams
Program Assumptions and Limitations:
1. The following references were used in the development of this program:
a. | Fluor Enterprises, Inc. - Guideline 000.215.1257 - "Hoisting Facilities" (August 22, 2005)
b. | Dupont Engineering Design Standard: DB1X - "Design and Installation of Monorail Beams" (May 2000)
c. | American National Standards Institute (ANSI): MH27.1 - "Underhung Cranes and Monorail Syatems"
d. | American Institute of Steel Construction (AISC) 9th Edition Allowable Stress Design (ASD) Manual (1989)
e. | "Allowable Bending Stresses for Overhanging Monorails" - by N. Stephen Tanner -
AISC Engineering Journal (3rd Quarter, 1985)
f. | Crane Manufacturers Association of America, Inc. (CMAA) - Publication No. 74 -
"Specifications for Top Running & Under Running Single Girder Electric Traveling Cranes
Utilizing Under Running Trolley Hoist" (2004)
g. | "Design of Monorail Systems" - by Thomas H. Orihuela Jr., PE (www.pdhengineer.com)
h. | British Steel Code B.S. 449, pages 42-44 (1959)
i. | USS Steel Design Manual - Chapter 7 "Torsion" - by R. L. Brockenbrough and B.G. Johnston (1981)
j. | AISC Steel Design Guide Series No. 9 - "Torsional Analysis of Structural Steel Members" -
by Paul A. Seaburg, PhD, PE and Charlie J. Carter, PE (1997)
k. | "Technical Note: Torsion Analysis of Steel Sections" - by William E. Moore II and Keith M. Mueller -
AISC Engineering Journal (4th Quarter, 2002)
2. The unbraced length for the overhang (cantilever) portion, 'Lbo', of an underhung monorail beam is often debated.
The following are some recommendations from the references cited above:
a. | Fluor Guideline 000.215.1257: Lbo = Lo+L/2
b. | Dupont Standard DB1X: Lbo = 3*Lo
c. | ANSI Standard MH27.1: Lbo = 2*Lo
d. | British Steel Code B.S. 449: Lbo = 2*Lo (for top flange of monorail beam restrained at support)
British Steel Code B.S. 449: Lbo = 3*Lo (for top flange of monorail beam unrestrained at support)
e. | AISC Eng. Journal Article by Tanner: Lbo = Lo+L (used with a computed value of 'Cbo' from article)
3. This program also determines the calculated value of the bending coefficient, 'Cbo', for the overhang (cantilever)
portion of the monorail beam from reference "e" in note #1 above. This is located off of the main calculation page.
Note: if this computed value of 'Cbo' is used and input, then per this reference the total value of Lo+L should be
used for the unbraced length, 'Lbo', for the overhang portion of the monorail beam.
4. This program ignores effects of axial compressive stress produced by any longitudinal (traction) force which is
usually considered minimal for underhung, hand-operated monorail systems.
5. This program contains “comment boxes” which contain a wide variety of information including explanations of
input or output items, equations used, data tables, etc. (Note: presence of a “comment box” is denoted by a
“red triangle” in the upper right-hand corner of a cell. Merely move the mouse pointer to the desired cell to view
the contents of that particular "comment box".)

## S-shaped Monorail Beam
MONORAIL BEAM ANALYSIS | [10 empty] | CALCULATIONS: | [27 empty] | Version 2.1
For S-shaped Underhung Monorails Analyzed as Simple-Spans with / without Overhang
Per AISC 9th Edition ASD Manual and CMAA Specification No. 74 (2004) | [9 empty] | 33 | Parameters and Coefficients: | [9 empty] | S-shape Section Properties from AISC Version 3.0 CD Database (2001) and AISC 9th Edition Manual (1989)
Job Name: |  |  |  |  | Subject: |  |  |  |  | 36 | w = | 50 | plf | unit weight/foot of beam | [6 empty] | Shape | A | d | tw | bf | tf | k | rt | d/Af | Ix | Sx | rx | Iy | Sy | ry | J | Cw | w | SUMMARY OF CHECKS:
Job Number: |  |  |  |  | Originator: |  |  | Checker: |  | 50 | Pv = | 7.4 | kips | Pv = P*(1+Vi/100)+Wt+Wh (vertical load) | [6 empty] | S24x121 | 35.5 | 24.5 | 0.8 | 8.05 | 1.09 | 2 | 1.86 | 2.79 | 3160 | 258 | 9.43 | 83 | 20.6 | 1.53 | 12.8 | 11400 | 121 | Row No.: | Results: |  |  | Stress Ratio:
[10 empty] | 2 | Pw = | 1.85 | kips/wheel | Pw = Pv/Nw (load per trolley wheel) | [6 empty] | S24x106 | 31.1 | 24.5 | 0.62 | 7.87 | 1.09 | 2 | 1.86 | 2.86 | 2940 | 240 | 9.71 | 76.8 | 19.5 | 1.57 | 10.1 | 10500 | 106 | Simple-Span Stresses and Deflection:
Input: | [9 empty] | 4 | Ph = | 0.6 | kips | Ph = HLF*P (horizontal load) | [6 empty] | S24x100 | 29.3 | 24 | 0.745 | 7.25 | 0.87 | 1.75 | 1.59 | 3.81 | 2380 | 199 | 9.01 | 47.4 | 13.1 | 1.27 | 7.59 | 6340 | 100 | 54 | fbx <= Fbx, O.K. |  |  | 0.42676
|  |  |  | RL(min)=-0.73 k |  |  | RR(max)=9.13 k |  |  |  | ta = | 0.49317 | in. | ta = tf-bf/24+a/6 (for S-shape) | [6 empty] | S24x90 | 26.5 | 24 | 0.625 | 7.13 | 0.87 | 1.75 | 1.6 | 3.87 | 2250 | 187 | 9.21 | 44.7 | 12.5 | 1.3 | 6.05 | 5980 | 90 | 61 | fby <= Fby, O.K. |  |  | 0.23524
Monorail Size: |  |  |  |  | L=17' |  | Lo=3' |  |  |  | l = | 0.15648 |  | l = 2*a/(bf-tw) | [6 empty] | S24x80 | 23.5 | 24 | 0.5 | 7 | 0.87 | 1.75 | 1.61 | 3.94 | 2100 | 175 | 9.47 | 42 | 12 | 1.34 | 4.89 | 5620 | 80 | 64 | S.R.(combined) <= 1.0, O.K. |  |  | 0.662
| Select: | S12x50 |  | x=8.313' | [6 empty] | Cxo = | -0.84957 |  | Cxo = -1.096+1.095*l+0.192*e^(-6.0*l) | [6 empty] | S20x96 | 28.2 | 20.3 | 0.8 | 7.2 | 0.92 | 1.75 | 1.63 | 3.06 | 1670 | 165 | 7.71 | 49.9 | 13.9 | 1.33 | 8.4 | 4690 | 96 | 70 | Defl.(max) <= Defl.(allow), O.K. |  |  | 0.31136
Design Parameters: |  |  |  |  | S=0.75' | [5 empty] | Cx1 = | 0.59953 |  | Cx1 = 3.965-4.835*l-3.965*e^(-2.675*l) | [6 empty] | S20x86 | 25.3 | 20.3 | 0.66 | 7.06 | 0.92 | 1.75 | 1.63 | 3.13 | 1570 | 155 | 7.89 | 46.6 | 13.2 | 1.36 | 6.65 | 4380 | 86 | Overhang Stresses and Deflection:
| Beam Fy = | 36 | ksi | [7 empty] | Czo = | 0.16496 |  | Czo = -0.981-1.479*l+1.120*e^(1.322*l) | [6 empty] | S20x75 | 22 | 20 | 0.635 | 6.39 | 0.795 | 1.625 | 1.43 | 3.94 | 1280 | 128 | 7.62 | 29.5 | 9.25 | 1.16 | 4.59 | 2720 | 75 | 84 | fbx <= Fbx, O.K. |  |  | 0.21574
| Beam Simple-Span, L = | 17 | ft. |  |  |  | S12x50 |  |  |  | Cz1 = | 1.9478 |  | Cz1 = 1.810-1.150*l+1.060*e^(-7.70*l) | [6 empty] | S20x66 | 19.4 | 20 | 0.505 | 6.26 | 0.795 | 1.625 | 1.44 | 4.02 | 1190 | 119 | 7.83 | 27.5 | 8.78 | 1.19 | 3.58 | 2540 | 66 | 90 | fby <= Fby, O.K. |  |  | 0.20632
| Unbraced Length, Lb = | 17 | ft. |  |  |  | Note: sketch depicts Nw = 4, |  |  |  | Section Ratios and Parameters: | [9 empty] | S18x70 | 20.5 | 18 | 0.711 | 6.25 | 0.691 | 1.5 | 1.36 | 4.17 | 923 | 103 | 6.7 | 24 | 7.69 | 1.08 | 4.1 | 1800 | 70 | 93 | S.R.(combined) <= 1.0, O.K. |  |  | 0.42206
| Bending Coef., Cb = | 1 |  |  | Pv=7.4 k |  | for 2-pairs of wheels. |  |  |  | bf/(2*tf) = | 4.1578 | [8 empty] | S18x54.7 | 16 | 18 | 0.461 | 6 | 0.691 | 1.5 | 1.37 | 4.34 | 801 | 89 | 7.07 | 20.7 | 6.91 | 1.14 | 2.33 | 1550 | 54.7 | 99 | Defl.(max) <= Defl.(allow), O.K. |  |  | 0.89385
| Overhang Length, Lo = | 3 | ft. | Nomenclature | [6 empty] | d/tw = | 17.4672 | [8 empty] | S15x50 | 14.7 | 15 | 0.55 | 5.64 | 0.622 | 1.375 | 1.26 | 4.28 | 485 | 64.7 | 5.75 | 15.6 | 5.53 | 1.03 | 2.12 | 806 | 50 | Bottom Flange Bending (simplified):
| Unbraced Length, Lbo = | 11.5 | ft. | [7 empty] | Qs = | 1 | [8 empty] | S15x42.9 | 12.6 | 15 | 0.411 | 5.5 | 0.622 | 1.375 | 1.26 | 4.38 | 446 | 59.4 | 5.95 | 14.3 | 5.19 | 1.06 | 1.54 | 739 | 42.9 | 108 | fb <= Fb = 0.75*Fy, O.K. |  |  | 0.1727
| Bending Coef., Cbo = | 1 |  | S12x50 Member Properties: | [6 empty] | Support Reactions: | [9 empty] | S12x50 | 14.6 | 12 | 0.687 | 5.48 | 0.659 | 1.4375 | 1.25 | 3.32 | 303 | 50.6 | 4.55 | 15.6 | 5.69 | 1.03 | 2.77 | 502 | 50 | Bottom Flange Bending (per CMAA No. 74):
| Lifted Load, P = | 6 | kips | A = | 14.6 | in.^2 | d/Af = | 3.32 |  |  | For Lo = 0 (no overhang): | [9 empty] | S12x40.8 | 11.9 | 12 | 0.462 | 5.25 | 0.659 | 1.4375 | 1.24 | 3.46 | 270 | 45.1 | 4.76 | 13.5 | 5.13 | 1.06 | 1.69 | 434 | 40.8 | 129 | fto <= Fb = 0.66*Fy, O.K. |  |  | 0.51801
| Trolley Weight, Wt = | 0.4 | kips | d = | 12 | in. | Ix = | 303 | in.^4 |  | RR(max) = | N.A. | kips | RR(max) = | N.A. | [5 empty] | S12x35 | 10.2 | 12 | 0.428 | 5.08 | 0.544 | 1.1875 | 1.16 | 4.34 | 228 | 38.1 | 4.72 | 9.84 | 3.88 | 0.98 | 1.05 | 323 | 35 | 136 | ft1 <= Fb = 0.66*Fy, O.K. |  |  | 0.90924
| Hoist Weight, Wh = | 0.1 | kips | tw = | 0.687 | in. | Sx = | 50.6 | in.^3 |  | RL(min) = | N.A. | kips | RL(min) = | N.A. | [5 empty] | S12x31.8 | 9.31 | 12 | 0.35 | 5 | 0.544 | 1.1875 | 1.16 | 4.41 | 217 | 36.2 | 4.83 | 9.33 | 3.73 | 1 | 0.878 | 306 | 31.8 | 143 | ft2 <= Fb = 0.66*Fy, O.K. |  |  | 0.24473
| Vert. Impact Factor, Vi = | 15 | % | bf = | 5.48 | in. | Iy = | 15.6 | in.^4 |  | For Lo > 0 (with overhang): | [9 empty] | S10x35 | 10.3 | 10 | 0.594 | 4.94 | 0.491 | 1.125 | 1.1 | 4.12 | 147 | 29.4 | 3.78 | 8.3 | 3.36 | 0.899 | 1.29 | 188 | 35
| Horz. Load Factor, HLF = | 10 | % | tf = | 0.659 | in. | Sy = | 5.69 | in.^3 |  | RR(max) = | 9.1309 | kips | RR(max) = | Pv*(L+(Lo-S/2))/L+w/1000/(2*L)*(L+Lo)^2 | [5 empty] | S10x25.4 | 7.45 | 10 | 0.311 | 4.66 | 0.491 | 1.125 | 1.09 | 4.37 | 123 | 24.6 | 4.07 | 6.73 | 2.89 | 0.95 | 0.603 | 152 | 25.4
| Total No. Wheels, Nw = | 4 | (2-pairs) | k= | 1.4375 | in. | J = | 2.77 | in.^4 |  | RL(min) = | -0.73088 | kips | RL(min) = | -Pv*(Lo-S/2)/L+w/1000/(2*L)*(L^2-Lo^2) | [5 empty] | S8x23 | 6.76 | 8 | 0.441 | 4.17 | 0.425 | 1 | 0.95 | 4.51 | 64.7 | 16.2 | 3.09 | 4.27 | 2.05 | 0.795 | 0.55 | 61.3 | 23 | From: "Allowable Bending Stresses for Overhanging Monorails"
| Wheel Spacing, S = | 0.75 | ft. | rt = | 1.25 | in. | Cw = | 502 | in.^6 |  | Bending Moments for Simple-Span: | [9 empty] | S8x18.4 | 5.4 | 8 | 0.271 | 4 | 0.425 | 1 | 0.95 | 4.7 | 57.5 | 14.4 | 3.26 | 3.69 | 1.84 | 0.827 | 0.335 | 52.9 | 18.4 | by N. Stephen Tanner - AISC Engineering Journal (3rd Quarter, 1985)
| Distance on Flange, a = | 0.375 | in. | [7 empty] | x = | 8.3125 | ft. | x = 1/2*(L-S/2) (location of max. moments from left end of simple-span) | [6 empty] | S7x20 | 5.88 | 7 | 0.45 | 3.86 | 0.392 | 0.9375 | 0.88 | 4.63 | 42.4 | 12.1 | 2.69 | 3.17 | 1.64 | 0.734 | 0.45 | 34.6 | 20 |  | Use: Lbo = Lo+L = | 20 | ft. |  | Table 1: Computed Values
|  |  |  | Support Reactions: |  | (with overhang) |  |  |  |  | Mx = | 31.8832 | ft-kips | Mx = (Pv/2)/(2*L)*(L-S/2)^2+w/1000*x/2*(L-x) | [6 empty] | S7x15.3 | 4.5 | 7 | 0.252 | 3.662 | 0.392 | 0.9375 | 0.87 | 4.88 | 36.7 | 10.5 | 2.86 | 2.64 | 1.44 | 0.766 | 0.24 | 28.8 | 15.3 |  | K = Lo/(Lo+L) = | 0.15 |  | Index | k = Lo/(Lo+L) | Cbo
Results: |  |  |  | RR(max) = | 9.1309 | = Pv*(L+(Lo-S/2))/L+w/1000/(2*L)*(L+Lo)^2 |  |  |  |  | My = | 2.4387 | ft-kips | My = (Ph/2)/(2*L)*(L-S/2)^2 | [6 empty] | S6x17.25 | 5.06 | 6 | 0.465 | 3.57 | 0.359 | 0.8125 | 0.81 | 4.69 | 26.2 | 8.74 | 2.28 | 2.29 | 1.28 | 0.673 | 0.371 | 18.2 | 17.25 |  | Use: Cbo = | 0.715 |  | 1 | 0 | 0.67
|  |  |  | RL(min) = | -0.73088 | = -Pv*(Lo-S/2)/L+w/1000/(2*L)*(L^2-Lo^2) |  |  |  |  | Lateral Flange Bending Moment from Torsion for Simple-Span: |  |  |  |  | (per USS Steel Design Manual, 1981) |  |  |  |  | S6x12.5 | 3.66 | 6 | 0.232 | 3.33 | 0.359 | 0.8125 | 0.79 | 5.02 | 22 | 7.34 | 2.45 | 1.8 | 1.08 | 0.702 | 0.167 | 14.3 | 12.5 |  |  |  |  | 2 | 0.1 | 0.7
Parameters and Coefficients: | [10 empty] | e = | 6 | in. | e = d/2 (assume horiz. load taken at bot. flange) | [6 empty] | S5x14.75 | 4.34 | 5 | 0.494 | 3.284 | 0.326 | 0.8125 | 0.74 | 4.66 | 15.2 | 6.09 | 1.87 | 1.67 | 1.01 | 0.62 | 0.32 | 9.12 | 14.75 |  |  |  |  | 3 | 0.2 | 0.73
Pv = | 7.4 | kips | Pv = P*(1+Vi/100)+Wt+Wh (vertical load) | [7 empty] | at = | 21.6622 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | [6 empty] | S5x10 | 2.93 | 5 | 0.214 | 3 | 0.326 | 0.75 | 0.72 | 5.1 | 12.3 | 4.9 | 2.05 | 1.19 | 0.795 | 0.638 | 0.114 | 6.5 | 10 |  |  |  |  | 4 | 0.3 | 0.76
Pw = | 1.85 | kips/wheel | Pw = Pv/Nw (load per trolley wheel) | [7 empty] | Mt = | 0.28646 | ft-kips | Mt = Ph*e*at/(2*(d-tf))*TANH(L*12/(2*at))/12 | [6 empty] | S4x9.5 | 2.79 | 4 | 0.326 | 2.8 | 0.293 | 0.75 | 0.65 | 4.88 | 6.76 | 3.38 | 1.56 | 0.887 | 0.635 | 0.564 | 0.12 | 3.05 | 9.5 |  |  |  |  | 5 | 0.4 | 0.8
Ph = | 0.6 | kips | Ph = HLF*P (horizontal load) | [7 empty] | X-axis Stresses for Simple-Span: | [9 empty] | S4x7.7 | 2.26 | 4 | 0.193 | 2.66 | 0.293 | 0.75 | 0.64 | 5.13 | 6.05 | 3.03 | 1.64 | 0.748 | 0.562 | 0.576 | 0.0732 | 2.57 | 7.7 |  |  |  |  | 6 | 0.5 | 0.84
ta = | 0.49317 | in. | ta = tf-bf/24+a/6 (for S-shape) | [7 empty] | fbx = | 7.5612 | ksi | fbx = Mx/Sx | [6 empty] | S3x7.5 | 2.2 | 3 | 0.349 | 2.51 | 0.26 | 0.625 | 0.59 | 4.6 | 2.91 | 1.94 | 1.15 | 0.578 | 0.461 | 0.513 | 0.0896 | 1.08 | 7.5 |  |  |  |  | 7 | 0.6 | 0.9
l = | 0.15648 |  | l = 2*a/(bf-tw) | [7 empty] | Lc = | 5.7844 | ft. | Lc = Min. of: (76*bf/SQRT(Fy))/12 or (20000/(d/Af*Fy))/12 | [6 empty] | S3x5.7 | 1.66 | 3 | 0.17 | 2.33 | 0.26 | 0.625 | 0.57 | 4.95 | 2.5 | 1.67 | 1.23 | 0.447 | 0.383 | 0.518 | 0.0433 | 0.839 | 5.7 |  |  |  |  | 8 | 0.7 | 0.96
Cxo = | -0.84957 |  | Cxo = -1.096+1.095*l+0.192*e^(-6.0*l) | [7 empty] | Lu = | 13.9447 | ft. | Lu = Max. of: (20000/(d/Af*Fy))/12 or (SQRT(102000/Fy)*rt)/12 | [28 empty] | 9 | 0.8 | 1.05
Cx1 = | 0.59953 |  | Cx1 = 3.965-4.835*l-3.965*e^(-2.675*l) | [7 empty] | Lb/rt = | 163.2 |  | Lb/rt = Lb*12/rt | [28 empty] | 10 | 0.9 | 1.15
Czo = | 0.16496 |  | Czo = -0.981-1.479*l+1.120*e^(1.322*l) | [7 empty] | fa/Fy = | 0 |  | fa/Fy = 0, as P(axial) is assumed = 0 | [28 empty] | 11 | 1 | 1.28
Cz1 = | 1.9478 |  | Cz1 = 1.810-1.150*l+1.060*e^(-7.70*l) | [7 empty] | Is Lb<=Lc? | No | [30 empty] | 2 | 0.1 | 0.7
[11 empty] | Is d/tw<=allow? | Yes | [30 empty] | 3 | 0.2 | 0.73
Bending Moments for Simple-Span: | [10 empty] | Is b/t<=65/SQRT(Fy)? | Yes
x = | 8.3125 | ft. | x = 1/2*(L-S/2) (location of max. moments from left end of simple-span) | [7 empty] | Is b/t>95/SQRT(Fy)? | No |  |  |  |  | Note: the calculation below is only used as a comparison/check against the main calculation to the left.
Mx = | 31.8832 | ft-kips | Mx = (Pv/2)/(2*L)*(L-S/2)^2+w/1000*x/2*(L-x) | [7 empty] | Fbx = | N.A. | Eqn. F1-1 | Fbx = 0.66*Fy |  |  | Torsion Analysis for Simple-Span per AISC Design Guide Series No. 9, Case 3:
My = | 2.4387 | ft-kips | My = (Ph/2)/(2*L)*(L-S/2)^2 | [7 empty] | Fbx = | N.A. | Eqn. F1-3 | Fbx = Fy*(0.79-0.002*bf/(2*tf)*SQRT(Fy)) |  |  | e = | 6 | in. | e = d/2
[11 empty] | Fbx = | N.A. | Eqn. F1-5 | Fbx = 0.60*Fy |  |  | T = | 3.6 | in.-kips | T = Ph*e
Lateral Flange Bending Moment from Torsion for Simple-Span: | [5 empty] | (per USS Steel Design Manual, 1981) |  |  |  |  | Fbx = | N.A. | Eqn. F1-6 | Fbx = (2/3-Fy*(Lb*12/rt)^2/(1530000*Cb)*Fy <= 0.60*Fy |  |  | at = | 21.6622 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi
e = | 6 | in. | e = d/2 (assume horiz. load taken at bot. flange) | [7 empty] | Fbx = | 6.3828 | Eqn. F1-7 | Fbx = 170000*Cb/(Lb*12/rt)^2 <= 0.60*Fy |  |  | Wns = | 15.5372 | in.^2 | Wns = (d-tf)*bf/4
at = | 21.6622 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | [7 empty] | Fbx = | 17.7179 | Eqn. F1-8 | Fbx = 12000*Cb/(Lb*12*(d/Af)) <= 0.60*Fy |  |  | a = | 0.5 |  | a = 0.500 (torque assumed at midspan)
Mt = | 0.28646 | ft-kips | Mt = Ph*e*at/(2*(d-tf))*TANH(L*12/(2*at))/12 | [7 empty] | Fbx = | 17.7179 | Select from F1-6, F1-7, & F1-8 |  |  |  | z = | 102 | in. | z = L*12/2 (calculated at midspan)
[11 empty] | Use: Fbx = | 17.7179 | ksi |  |  |  | c1 = | 0.00011604 |  | c1 = T/(J*G)
X-axis Stresses for Simple-Span: | [10 empty] | Y-axis Stresses for Simple-Span: | [5 empty] | c2 = | -0.009016 |  | c2 = SINH(a*L*12/at)/TANH(L*12/at)-COSH(a*L*12/at)
fbx = | 7.5612 | ksi | fbx = Mx/Sx | [7 empty] | fby = | 5.1432 | ksi | fby = My/Sy |  |  | q'' = | -2.6779e-06 |  | q'' = c1*c2/at*SINH(z/at)
Lb/rt = | 163.2 |  | Lb/rt = Lb*12/rt | [7 empty] | fwns = | 1.2083 | ksi | fwns = Mt*12/(Sy/2) (warping normal stress) |  |  | sn = | 1.2066 | ksi | sn = ABS(E*Wns*q'') (warping normal stress)
Fbx = | 17.7179 | ksi | Fbx = 12000*Cb/(Lb*12*(d/Af)) <= 0.60*Fy | [5 empty] | fbx <= Fbx, O.K. |  | fby(total) = | 6.3515 | ksi | fby(total) = fby+fwns | [24 empty] | SR = | 0.42676
[9 empty] | (continued) |  | Fby = | 27 | ksi | Fby = 0.75*Fy
Combined Stress Ratio for Simple-Span:
Y-axis Stresses for Simple-Span: | [10 empty] | S.R. = | 0.662 |  | S.R. = fbx/Fbx+fby(total)/Fby
fby = | 5.1432 | ksi | fby = My/Sy | [7 empty] | Vertical Deflection for Simple-Span:
fwns = | 1.2083 | ksi | fwns = Mt*12/(Sy/2) (warping normal stress) | [7 empty] | Pv = | 6.5 | kips | Pv = P+Wh+Wt (without vertical impact)
fby(total) = | 6.3515 | ksi | fby(total) = fby+fwns | [7 empty] | D(max) = | 0.14115 | in. | D(max) = | (Pv/2)*(L-S)/2/(24*E*I)*(3*L^2-4*((L-S)/2)^2)+5*w/12000*L^4/(384*E*I)
Fby = | 27 | ksi | Fby = 0.75*Fy | [5 empty] | fby <= Fby, O.K. |  | D(ratio) = | L/1445 |  | D(ratio) = L*12/D(max) | [24 empty] | SR = | 0.23524
[11 empty] | D(allow) = | 0.45333 | in. | D(allow) = L*12/450
Combined Stress Ratio for Simple-Span: | [10 empty] | Bending Moments for Overhang:
S.R. = | 0.662 |  | S.R. = fbx/Fbx+fby(total)/Fby | [5 empty] | S.R. <= 1.0, O.K. |  | Mx = | 19.65 | ft-kips | Mx = (Pv/2)*(Lo+(Lo-S))+w/1000*Lo^2/2 | [24 empty] | SR = | 0.662
[11 empty] | My = | 1.575 | ft-kips | My = (Ph/2)*(Lo+(Lo-S))
Vertical Deflection for Simple-Span: | [10 empty] | Lateral Flange Bending Moment from Torsion for Overhang: |  |  |  |  | (per USS Steel Design Manual, 1981)
Pv = | 6.5 | kips | Pv = P+Wh+Wt (without vertical impact) | [7 empty] | e = | 6 | in. | e = d/2 (assume horiz. load taken at bot. flange)
D(max) = | 0.14115 | in. | D(max) = | (Pv/2)*(L-S)/2/(24*E*I)*(3*L^2-4*((L-S)/2)^2)+5*w/12000*L^4/(384*E*I) | [6 empty] | at = | 21.6622 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi
D(ratio) = | L/1445 |  | D(ratio) = L*12/D(max) | [7 empty] | Mt = | 0.53318 | ft-kips | Mt = Ph*e*at/(d-tf)*TANH(Lo*12/at)/12
D(allow) = | 0.45333 | in. | D(allow) = L*12/450 | [5 empty] | Defl.(max) <= Defl.(allow), O.K. |  | X-axis Stresses for Overhang: | [27 empty] | SR = | 0.31136
|  |  |  | (from CMAA Specification No. 74, Section 1.4.1.2) | [6 empty] | fbx = | 4.6601 | ksi | fbx = Mx/Sx
Bending Moments for Overhang: | [10 empty] | Lc = | 5.7844 | ft. | Lc = Min. of: (76*bf/SQRT(Fy))/12 or (20000/(d/Af*Fy))/12
Mx = | 19.65 | ft-kips | Mx = (Pv/2)*(Lo+(Lo-S))+w/1000*Lo^2/2 | [7 empty] | Lu = | 13.9447 | ft. | Lu = Max. of: (20000/(d/Af*Fy))/12 or (SQRT(102000/Fy)*rt)/12
My = | 1.575 | ft-kips | My = (Ph/2)*(Lo+(Lo-S)) | [7 empty] | Lbo/rt = | 110.4 |  | Lbo/rt = Lbo*12/rt
[11 empty] | fa/Fy = | 0 |  | fa/Fy = 0, as P(axial) is assumed = 0
Lateral Flange Bending Moment from Torsion for Overhang: | [5 empty] | (per USS Steel Design Manual, 1981) |  |  |  |  | Is Lbo<=Lc? | No
e = | 6 | in. | e = d/2 (assume horiz. load taken at bot. flange) | [7 empty] | Is d/tw<=allow? | Yes
at = | 21.6622 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | [7 empty] | Is b/t<=65/SQRT(Fy)? | Yes
Mt = | 0.53318 | ft-kips | Mt = Ph*e*at/(d-tf)*TANH(Lo*12/at)/12 | [7 empty] | Is b/t>95/SQRT(Fy)? | No |  |  |  |  | Note: the calculation below is only used as a comparison/check against the main calculation to the left.
[11 empty] | Fbx = | N.A. | Eqn. F1-1 | Fbx = 0.66*Fy |  |  | Torsion Analysis for Fixed-End Cantilever per AISC Design Guide Series No. 9, Case 9:
X-axis Stresses for Overhang: | [10 empty] | Fbx = | N.A. | Eqn. F1-3 | Fbx = Fy*(0.79-0.002*bf/(2*tf)*SQRT(Fy)) |  |  | e = | 6 | in. | e = d/2
fbx = | 4.6601 | ksi | fbx = Mx/Sx | [7 empty] | Fbx = | N.A. | Eqn. F1-5 | Fbx = 0.60*Fy |  |  | T = | 3.6 | in.-kips | T = Ph*e
Lbo/rt = | 110.4 |  | Lbo/rt = Lbo*12/rt | [7 empty] | Fbx = | 13.6759 | Eqn. F1-6 | Fbx = (2/3-Fy*(Lbo*12/rt)^2/(1530000*Cbo)*Fy <= 0.60*Fy |  |  | at = | 21.6622 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi
Fbx = | 21.6 | ksi | Fbx = 12000*Cbo/(Lbo*12*(d/Af)) <= 0.60*Fy |  |  |  |  | fbx <= Fbx, O.K. |  |  | Fbx = | N.A. | Eqn. F1-7 | Fbx = 170000*Cbo/(Lbo*12/rt)^2 <= 0.60*Fy |  |  | Wns = | 15.5372 | in.^2 | Wns = (d-tf)*bf/4 | [18 empty] | SR = | 0.21574
[11 empty] | Fbx = | 21.6 | Eqn. F1-8 | Fbx = 12000*Cbo/(Lbo*12*(d/Af)) <= 0.60*Fy |  |  | a = | 1 |  | a = 1.000 (torque assumed at free end of cantilever)
Y-axis Stresses for Overhang: | [10 empty] | Fbx = | 21.6 | Select from F1-6, F1-7, & F1-8 |  |  |  | z = | 0 | in. | z = Lo*12 (calculated at fixed end of cantilever)
fby = | 3.3216 | ksi | fby = My/Sy | [7 empty] | Use: Fbx = | 21.6 | ksi |  |  |  | c1 = | 0.00011604 |  | c1 = T/(J*G)
fwns = | 2.2489 | ksi | fwns = Mt*12/(Sy/2) (warping normal stress) | [7 empty] | Y-axis Stresses for Overhang: | [5 empty] | c2 = | 0.93047 |  | c2 = SINH(a*Lo*12/at)-TANH(Lo*12/at)*COSH(a*Lo*12/at)+TANH(Lo*12/at)
fby(total) = | 5.5705 | ksi | fby(total) = fby+fwns | [7 empty] | fby = | 3.3216 | ksi | fby = My/Sy |  |  | q'' = | 4.9843e-06 |  | q'' = c1/at*(c2*COSH(z/at)-SINH(z/at))
Fby = | 27 | ksi | Fby = 0.75*Fy |  |  |  |  | fby <= Fby, O.K. |  |  | fwns = | 2.2489 | ksi | fwns = Mt*12/(Sy/2) (warping normal stress) |  |  | sn = | 2.2458 | ksi | sn = ABS(E*Wns*q'') (warping normal stress) | [18 empty] | SR = | 0.20632
[11 empty] | fby(total) = | 5.5705 | ksi | fby(total) = fby+fwns
Combined Stress Ratio for Overhang: | [10 empty] | Fby = | 27 | ksi | Fby = 0.75*Fy
S.R. = | 0.42206 |  | S.R. = fbx/Fbx+fby(total)/Fby |  |  |  |  | S.R. <= 1.0, O.K. |  |  | Combined Stress Ratio for Overhang: | [27 empty] | SR = | 0.42206
[11 empty] | S.R. = | 0.42206 |  | S.R. = fbx/Fbx+fby(total)/Fby
Vertical Deflection for Overhang: |  |  | (for Nw = 4 and S < Lo, assume all of Pv without impact at end of overhang) | [7 empty] | Vertical Deflection for Overhang: |  |  | (for Nw = 4 and S < Lo, assume all of Pv without impact at end of overhang)
Pv = | 6.5 | kips | Pv = P+Wh+Wt (without vertical impact) | [7 empty] | Pv = | 6.5 | kips | Pv = P+Wh+Wt (without vertical impact)
D(max) = | 0.071508 | in. | D(max) = | Pv*Lo^2*(L+Lo)/(3*E*I)+w/12000*Lo*(4*Lo^2*L-L^3+3*Lo^3)/(24*E*I) | [6 empty] | D(max) = | 0.071508 | in. | D(max) = | Pv*Lo^2*(L+Lo)/(3*E*I)+w/12000*Lo*(4*Lo^2*L-L^3+3*Lo^3)/(24*E*I)
D(ratio) = | L/503 |  | D(ratio) = Lo*12/D(max) | [7 empty] | D(ratio) = | L/503 |  | D(ratio) = Lo*12/D(max)
D(allow) = | 0.08 | in. | D(allow) = Lo*12/450 | [5 empty] | Defl.(max) <= Defl.(allow), O.K. |  | D(allow) = | 0.08 | in. | D(allow) = Lo*12/450 | [24 empty] | SR = | 0.89385
Notes: Values of "L", "Lo", & "S" in equation above for D(max) are multiplied by 12.
Bottom Flange Bending (simplified): | [10 empty] | Bottom Flange Bending (simplified):
be = | 7.908 | in. | Min. of: be = 12*tf or S*12 (effective flange bending length) | [7 empty] | be = | 7.908 | in. | Min. of: be = 12*tf or S*12 (effective flange bending length)
tf2 = | 0.85871 | in. | tf2 = tf+(bf/2-tw/2)/2*(1/6) (flange thk. at web based on 1:6 slope of flange) | [7 empty] | tf2 = | 0.85871 | in. | tf2 = tf+(bf/2-tw/2)/2*(1/6) (flange thk. at web based on 1:6 slope of flange)
am = | 1.8177 | in. | am = (bf/2-tw/2)-(k-tf2) (where: k-tf2 = radius of fillet) | [7 empty] | am = | 1.8177 | in. | am = (bf/2-tw/2)-(k-tf2) (where: k-tf2 = radius of fillet)
Mf = | 2.669 | in.-kips | Mf = Pw*(am-a) | [7 empty] | Mf = | 2.669 | in.-kips | Mf = Pw*(am-a)
Sf = | 0.57238 | in.^3 | Sf = be*tf^2/6 | [7 empty] | Sf = | 0.57238 | in.^3 | Sf = be*tf^2/6
fb = | 4.663 | ksi | fb = Mf/Sf | [7 empty] | fb = | 4.663 | ksi | fb = Mf/Sf
Fb = | 27 | ksi | Fb = 0.75*Fy | [5 empty] | fb <= Fb, O.K. |  | Fb = | 27 | ksi | Fb = 0.75*Fy | [24 empty] | SR = | 0.1727
[11 empty] | Bottom Flange Bending per CMAA Specification No. 74 (2004): |  |  |  |  | (Note: torsion is neglected)
[9 empty] | (continued) |  | Local Flange Bending Stress @ Point 0: |  |  |  |  | (Sign convention: + = tension, - = compression)
[11 empty] | sxo = | -6.4623 | ksi | sxo = Cxo*Pw/ta^2
Bottom Flange Bending per CMAA Specification No. 74 (2004): | [5 empty] | (Note: torsion is neglected) |  |  |  |  | szo = | 1.2548 | ksi | szo = Czo*Pw/ta^2
Local Flange Bending Stress @ Point 1:
Local Flange Bending Stress @ Point 0: | [8 empty] | (Sign convention: + = tension, - = compression) |  | sx1 = | 4.5603 | ksi | sx1 = Cx1*Pw/ta^2
sxo = | -6.4623 | ksi | sxo = Cxo*Pw/ta^2 | [7 empty] | sz1 = | 14.8156 | ksi | sz1 = Cz1*Pw/ta^2
szo = | 1.2548 | ksi | szo = Czo*Pw/ta^2 | [7 empty] | Local Flange Bending Stress @ Point 2:
Local Flange Bending Stress @ Point 1: | [10 empty] | sx2 = | 6.4623 | ksi | sx2 = -sxo
sx1 = | 4.5603 | ksi | sx1 = Cx1*Pw/ta^2 | [7 empty] | sz2 = | -1.2548 | ksi | sz2 = -szo
sz1 = | 14.8156 | ksi | sz1 = Cz1*Pw/ta^2 | [7 empty] | Resultant Biaxial Stress @ Point 0:
Local Flange Bending Stress @ Point 2: | [10 empty] | fbxo = | 7.5612 | ksi | fbxo = Mx*(d/2)/Ix = Mx/Sx
sx2 = | 6.4623 | ksi | sx2 = -sxo | [7 empty] | fbyo = | 0.64439 | ksi | fbyo = My*(tw/2)/Iy
sz2 = | -1.2548 | ksi | sz2 = -szo | [7 empty] | sz = | 9.1467 | ksi | sz = fbxo+fbyo+0.75*szo
Resultant Biaxial Stress @ Point 0: | [10 empty] | sx = | -4.8467 | ksi | sx = 0.75*sxo
fbxo = | 7.5612 | ksi | fbxo = Mx*(d/2)/Ix = Mx/Sx | [7 empty] | txz = | 0 | ksi | txz = 0 (assumed negligible)
fbyo = | 0.64439 | ksi | fbyo = My*(tw/2)/Iy | [7 empty] | sto = | 12.3079 | ksi | sto = SQRT(sx^2+sz^2-sx*sz+3*txz^2)
sz = | 9.1467 | ksi | sz = fbxo+fbyo+0.75*szo | [7 empty] | Resultant Biaxial Stress @ Point 1:
sx = | -4.8467 | ksi | sx = 0.75*sxo | [7 empty] | fbx1 = | 7.5612 | ksi | fbx1 = Mx*(d/2)/Ix = Mx/Sx
txz = | 0 | ksi | txz = 0 (assumed negligible) | [7 empty] | fby1 = | 4.4366 | ksi | fby1 = My*(bf/2-a)/Iy
sto = | 12.3079 | ksi | sto = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [5 empty] | <= Fb = 0.66*Fy = 23.76 ksi, O.K. |  | sz = | 23.1096 | ksi | sz = fbx1+fby1+0.75*sz1 | [24 empty] | SR = | 0.51801
Resultant Biaxial Stress @ Point 1: | [10 empty] | sx = | 3.4203 | ksi | sx = 0.75*sx1
fbx1 = | 7.5612 | ksi | fbx1 = Mx*(d/2)/Ix = Mx/Sx | [7 empty] | txz = | 0 | ksi | txz = 0 (assumed negligible)
fby1 = | 4.4366 | ksi | fby1 = My*(bf/2-a)/Iy | [7 empty] | st1 = | 21.6035 | ksi | st1 = SQRT(sx^2+sz^2-sx*sz+3*txz^2)
sz = | 23.1096 | ksi | sz = fbx1+fby1+0.75*sz1 | [7 empty] | Resultant Biaxial Stress @ Point 2:
sx = | 3.4203 | ksi | sx = 0.75*sx1 | [7 empty] | fbx2 = | 6.7441 | ksi | fbx2 = Mx*(d/2-tf)/Ix
txz = | 0 | ksi | txz = 0 (assumed negligible) | [7 empty] | fby2 = | 0.64439 | ksi | fby2 = My*(tw/2)/Iy
st1 = | 21.6035 | ksi | st1 = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [5 empty] | <= Fb = 0.66*Fy = 23.76 ksi, O.K. |  | sz = | 6.4474 | ksi | sz = fbx2+fby2+0.75*sz2 | [24 empty] | SR = | 0.90924
Resultant Biaxial Stress @ Point 2: | [10 empty] | sx = | 4.8467 | ksi | sx = 0.75*sx2
fbx2 = | 6.7441 | ksi | fbx2 = Mx*(d/2-tf)/Ix | [7 empty] | txz = | 0 | ksi | txz = 0 (assumed negligible)
fby2 = | 0.64439 | ksi | fby2 = My*(tw/2)/Iy | [7 empty] | st2 = | 5.8147 | ksi | st2 = SQRT(sx^2+sz^2-sx*sz+3*txz^2)
sz = | 6.4474 | ksi | sz = fbx2+fby2+0.75*sz2
sx = | 4.8467 | ksi | sx = 0.75*sx2
txz = | 0 | ksi | txz = 0 (assumed negligible)
st2 = | 5.8147 | ksi | st2 = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [5 empty] | <= Fb = 0.66*Fy = 23.76 ksi, O.K. | [29 empty] | SR = | 0.24473
Note on BA1: "MONORAIL.xls" written by: Alex Tomanovich, P.E.
Note on C17: The unbraced length for the overhang (cantilever) portion, 'Lbo', is often debated. Here are some recommendations from different sources: 1. Per Fluor Enterprises Guideline 000.215.1257 - "Hoisting Facilities" Lbo = Lo+L/2 2. Per Dupont Standard DB1X - "Design and Installation of Monorail Beams" Lbo = 3*Lo 3. Per ANSI MH27.1 - "Underhung Cranes and Monorail Systems" Lbo = 2*Lo 4. Per British Steel Code B.S. 449, pages 42-44 (1959) Lbo = 2*Lo (for top flange of monorail beam restrained at support) Lbo = 3*Lo (for top flange of monorail beam unrestrained at support) 5. Per AISC Journal article by N. Stephen Tanner - "Allowable Bending Stresses for Overhanging Monorails" (3rd Quarter, 1985) Lbo = Lo+L (used with a computed value of 'Cbo' from article)
Note on BC26: If this user elects to use this reference for the analysis of the overhang (cantilever) portion of the monorqil beam, then this value of Lbo = Lo+L should be input into cell C17.
Note on BG26: Table 1 is reproduced from page 137 of the referenced article.
Note on BC28: If this user elects to use this reference for the analysis of the overhang (cantilever) portion of the monorail beam, then this computed value of 'Cbo', interpolated from Table 1, should be input into cell C18.
Note on F28: For a monorail consisting of a simple-span with no overhang, 'RR(max)' and 'RL(min)' are determined by positioning the trolley at the right support. For a monorail consisting of a simple-span with an overhang, 'RR(max)' and 'RL(min)' are determined by positioning the trolley at the end of the overhang. The self-weight of the monorail beam is also included.
Note on F29: For a monorail consisting of a simple-span with no overhang, 'RR(max)' and 'RL(min)' are determined by positioning the trolley at the right support. For a monorail consisting of a simple-span with an overhang, 'RR(max)' and 'RL(min)' are determined by positioning the trolley at the end of the overhang. The self-weight of the monorail beam is also included.
Note on C15: From AISC 9th Edition ASD Manual, page 5-47: 'Cb' is the allowable stress bending coefficient dependent on the moment gradient, for bending about the X-axis (major axis). 'Cb' is determined as follows: Cb = 1.75+1.05*(Mx1/Mx2)+0.3*(Mx1/Mx2)^2 <= 2.3 where: Mx1 = smaller X-axis (major axis) bending moment at either of the ends of the unbraced length Mx2 = larger X-axis (major axis) bending moment at either of the ends of the unbraced length Mx1/Mx2 = positive for reverse curvature bending (both have same signs) = negative for single curvature bending (both have opposite signs) Note: 1. When the bending moment at any point within an unbraced length is larger than that at both ends of this length, then use 'Cb' = 1.0.
Note on B70: Note: a Vertical Deflection criteria of L/450 is assumed to be used, and is taken from CMAA Specification No. 74, per Section 1.4.1.2 for "Under-Running Runways".
bf
ta
tw
bf/4
tf
X
Z
Y
Pw
Pw
Pw
Pw
Trolley Wheel
S-shape
tw/2
Point 2
Point 0
Point 1

## W-shaped Monorail Beam
MONORAIL BEAM ANALYSIS | [10 empty] | CALCULATIONS: | [27 empty] | Version 2.1
For W-shaped Underhung Monorails Analyzed as Simple-Spans with / without Overhang
Per AISC 9th Edition ASD Manual and CMAA Specification No. 74 (2004) | [9 empty] | 33 | Parameters and Coefficients: | [9 empty] | W-shape Section Properties from AISC Version 3.0 CD Database (2001) and AISC 9th Edition Manual (1989)
Job Name: |  |  |  |  | Subject: |  |  |  |  | 36 | w = | 50 | plf | unit weight/foot of beam | [6 empty] | Shape | A | d | tw | bf | tf | k | rt | d/Af | Ix | Sx | rx | Iy | Sy | ry | J | Cw | w | SUMMARY OF CHECKS:
Job Number: |  |  |  |  | Originator: |  |  | Checker: |  | 50 | Pv = | 7.4 | kips | Pv = P*(1+Vi/100)+Wt+Wh (vertical load) | [6 empty] | W44x335 | 98.3 | 44 | 1.02 | 16 | 1.77 | 2.56 | 4.12 | 1.56 | 31100 | 1410 | 17.8 | 1200 | 151 | 3.5 | 74.4 | 536000 | 335 | Row No.: | Results: |  |  | Stress Ratio:
[10 empty] | 2 | Pw = | 1.85 | kips/wheel | Pw = Pv/Nw (load per trolley wheel) | [6 empty] | W44x290 | 85.8 | 43.6 | 0.87 | 15.8 | 1.58 | 2.37 | 4.1 | 1.74 | 27100 | 1240 | 17.8 | 1050 | 132 | 3.49 | 51.5 | 464000 | 290 | Simple-Span Stresses and Deflection:
Input: | [9 empty] | 4 | Ph = | 0.6 | kips | Ph = HLF*P (horizontal load) | [6 empty] | W44x285 | 83.8 | 44.02 | 1.024 | 11.811 | 1.772 | 2.6875 | 2.95 | 2.1 | 24600 | 1120 | 17.1 | 490 | 83 | 2.42 | 60 | 219000 | 285 | 54 | fbx <= Fbx, O.K. |  |  | 0.2759
|  |  |  | RL(min)=-0.73 k |  |  | RR(max)=9.13 k |  |  |  | ta = | 0.64 | in. | ta = tf (for W-shape) | [6 empty] | W44x262 | 77.2 | 43.3 | 0.79 | 15.8 | 1.42 | 2.21 | 4.07 | 1.94 | 24200 | 1120 | 17.7 | 927 | 118 | 3.46 | 37.7 | 407000 | 262 | 61 | fby <= Fby, O.K. |  |  | 0.12106
Monorail Size: |  |  |  |  | L=17' |  | Lo=3' |  |  |  | l = | 0.097276 |  | l = 2*a/(bf-tw) | [6 empty] | W44x248 | 72.8 | 43.62 | 0.865 | 11.811 | 1.575 | 2.5 | 2.96 | 2.34 | 21400 | 983 | 17.2 | 435 | 74 | 2.44 | 40.7 | 192000 | 248 | 64 | S.R.(combined) <= 1.0, O.K. |  |  | 0.39696
| Select: | W12x50 |  | x=8.313' | [6 empty] | Cxo = | -1.9033 |  | Cxo = -2.110+1.977*l+0.0076*e^(6.53*l) | [6 empty] | W44x230 | 67.7 | 42.9 | 0.71 | 15.8 | 1.22 | 2.01 | 4.05 | 2.23 | 20800 | 971 | 17.5 | 796 | 101 | 3.43 | 24.9 | 346000 | 230 | 70 | Defl.(max) <= Defl.(allow), O.K. |  |  | 0.24129
Design Parameters: |  |  |  |  | S=0.75' | [5 empty] | Cx1 = | 0.53539 |  | Cx1 = 10.108-7.408*l-10.108*e^(-1.364*l) | [6 empty] | W44X224 | 65.8 | 43.31 | 0.787 | 11.811 | 1.416 | 2.3125 | 2.96 | 2.59 | 19200 | 889 | 17.1 | 391 | 66 | 2.44 | 30 | 172000 | 224 | Overhang Stresses and Deflection:
| Beam Fy = | 36 | ksi | [7 empty] | Czo = | 0.19202 |  | Czo = 0.050-0.580*l+0.148*e^(3.015*l) | [6 empty] | W44x198 | 58 | 42.91 | 0.709 | 11.811 | 1.22 | 2.125 | 2.94 | 2.98 | 16700 | 776 | 16.9 | 336 | 57 | 2.41 | 20.1 | 146000 | 198 | 84 | fbx <= Fbx, O.K. |  |  | 0.17004
| Beam Simple-Span, L = | 17 | ft. |  |  |  | W12x50 |  |  |  | Cz1 = | 2.3187 |  | Cz1 = 2.230-1.490*l+1.390*e^(-18.33*l) | [6 empty] | W40x655 | 192 | 43.62 | 1.97 | 16.87 | 3.54 | 4.9375 | 4.43 | 0.73 | 56500 | 2590 | 17.2 | 2860 | 339 | 3.86 | 596 | 1140000 | 655 | 90 | fby <= Fby, O.K. |  |  | 0.1033
| Unbraced Length, Lb = | 17 | ft. |  |  |  | Note: sketch depicts Nw = 4, |  |  |  | Section Ratios and Parameters: | [9 empty] | W40x593 | 174 | 43 | 1.79 | 16.7 | 3.23 | 4.41 | 4.38 | 0.8 | 50400 | 2340 | 17 | 2520 | 302 | 3.8 | 445 | 996000 | 593 | 93 | S.R.(combined) <= 1.0, O.K. |  |  | 0.27334
| Bending Coef., Cb = | 1 |  |  | Pv=7.4 k |  | for 2-pairs of wheels. |  |  |  | bf/(2*tf) = | 6.3125 | [8 empty] | W40x531 | 156 | 42.34 | 1.61 | 16.51 | 2.91 | 4.3125 | 4.33 | 0.88 | 44300 | 2090 | 16.9 | 2200 | 266 | 3.75 | 329 | 848000 | 531 | 99 | Defl.(max) <= Defl.(allow), O.K. |  |  | 0.69268
| Overhang Length, Lo = | 3 | ft. | Nomenclature | [6 empty] | d/tw = | 32.973 | [8 empty] | W40x503 | 148 | 42.1 | 1.54 | 16.4 | 2.76 | 3.94 | 4.3 | 0.93 | 41700 | 1980 | 16.8 | 2050 | 250 | 3.72 | 279 | 791000 | 503 | Bottom Flange Bending (simplified):
| Unbraced Length, Lbo = | 11.5 | ft. | [7 empty] | Qs = | 1 | [8 empty] | W40x480 | 140 | 41.81 | 1.46 | 16.36 | 2.64 | 4 | 4.28 | 0.97 | 39500 | 1890 | 16.8 | 1940 | 237 | 3.72 | 245 | 739000 | 480 | 107 | fb <= Fb = 0.75*Fy, O.K. |  |  | 0.38945
| Bending Coef., Cbo = | 1 |  | W12x50 Member Properties: | [6 empty] | Support Reactions: | [9 empty] | W40x466 | 137 | 42.44 | 1.67 | 12.64 | 2.95 | 4.125 | 3.22 | 1.14 | 36300 | 1710 | 16.3 | 1010 | 160 | 2.72 | 277 | 393000 | 466 | Bottom Flange Bending (per CMAA No. 74):
| Lifted Load, P = | 6 | kips | A = | 14.6 | in.^2 | d/Af = | 2.36 |  |  | For Lo = 0 (no overhang): | [9 empty] | W40x436 | 128 | 41.34 | 1.34 | 16.24 | 2.4 | 3.8125 | 4.24 | 1.06 | 35400 | 1710 | 16.6 | 1720 | 212 | 3.67 | 186 | 649000 | 436 | 129 | fto <= Fb = 0.66*Fy, O.K. |  |  | 0.47946
| Trolley Weight, Wt = | 0.4 | kips | d = | 12.2 | in. | Ix = | 391 | in.^4 |  | RR(max) = | N.A. | kips | RR(max) = | N.A. | [5 empty] | W40x431 | 127 | 41.3 | 1.34 | 16.2 | 2.36 | 3.54 | 4.23 | 1.08 | 34800 | 1690 | 16.6 | 1690 | 208 | 3.65 | 177 | 639000 | 431 | 136 | ft1 <= Fb = 0.66*Fy, O.K. |  |  | 0.62691
| Hoist Weight, Wh = | 0.1 | kips | tw = | 0.37 | in. | Sx = | 64.2 | in.^3 |  | RL(min) = | N.A. | kips | RL(min) = | N.A. | [5 empty] | W40x397 | 117 | 41 | 1.22 | 16.1 | 2.2 | 3.38 | 4.21 | 1.15 | 32000 | 1560 | 16.6 | 1540 | 191 | 3.64 | 142 | 578000 | 397 | 143 | ft2 <= Fb = 0.66*Fy, O.K. |  |  | 0.24406
| Vert. Impact Factor, Vi = | 15 | % | bf = | 8.08 | in. | Iy = | 56.3 | in.^4 |  | For Lo > 0 (with overhang): | [9 empty] | W40x392 | 115 | 41.6 | 1.42 | 12.4 | 2.52 | 3.7 | 3.14 | 1.33 | 29900 | 1440 | 16.1 | 803 | 130 | 2.64 | 172 | 306000 | 392
| Horz. Load Factor, HLF = | 10 | % | tf = | 0.64 | in. | Sy = | 13.9 | in.^3 |  | RR(max) = | 9.1309 | kips | RR(max) = | Pv*(L+(Lo-S/2))/L+w/1000/(2*L)*(L+Lo)^2 | [5 empty] | W40x372 | 109 | 40.6 | 1.16 | 16.1 | 2.05 | 3.23 | 4.18 | 1.23 | 29600 | 1460 | 16.5 | 1420 | 177 | 3.6 | 116 | 528000 | 372
| Total No. Wheels, Nw = | 4 | (2-pairs) | k= | 1.14 | in. | J = | 1.71 | in.^4 |  | RL(min) = | -0.73088 | kips | RL(min) = | -Pv*(Lo-S/2)/L+w/1000/(2*L)*(L^2-Lo^2) | [5 empty] | W40x362 | 107 | 40.6 | 1.12 | 16 | 2.01 | 3.19 | 4.17 | 1.26 | 28900 | 1420 | 16.5 | 1380 | 173 | 3.6 | 109 | 512000 | 362 | From: "Allowable Bending Stresses for Overhanging Monorails"
| Wheel Spacing, S = | 0.75 | ft. | rt = | 2.17 | in. | Cw = | 1880 | in.^6 |  | Bending Moments for Simple-Span: | [9 empty] | W40x331 | 97.5 | 40.8 | 1.22 | 12.2 | 2.13 | 3.31 | 3.08 | 1.57 | 24700 | 1210 | 15.9 | 644 | 106 | 2.57 | 106 | 241000 | 331 | by N. Stephen Tanner - AISC Engineering Journal (3rd Quarter, 1985)
| Distance on Flange, a = | 0.375 | in. | [7 empty] | x = | 8.3125 | ft. | x = 1/2*(L-S/2) (location of max. moments from left end of simple-span) | [6 empty] | W40x328 | 96.4 | 40 | 0.91 | 17.91 | 1.73 | 3.125 | 4.73 | 1.29 | 26800 | 1340 | 16.7 | 1660 | 185 | 4.15 | 74.2 | 607000 | 328 |  | Use: Lbo = Lo+L = | 20 | ft. |  | Table 1: Computed Values
|  |  |  | Support Reactions: |  | (with overhang) |  |  |  |  | Mx = | 31.8832 | ft-kips | Mx = (Pv/2)/(2*L)*(L-S/2)^2+w/1000*x/2*(L-x) | [6 empty] | W40x327 | 96 | 40.8 | 1.18 | 12.1 | 2.13 | 3.31 | 3.09 | 1.58 | 24500 | 1200 | 16 | 640 | 105 | 2.58 | 103 | 239000 | 327 |  | K = Lo/(Lo+L) = | 0.15 |  | Index | k = Lo/(Lo+L) | Cbo
Results: |  |  |  | RR(max) = | 9.1309 | = Pv*(L+(Lo-S/2))/L+w/1000/(2*L)*(L+Lo)^2 |  |  |  |  | My = | 2.4387 | ft-kips | My = (Ph/2)/(2*L)*(L-S/2)^2 | [6 empty] | W40x324 | 95.3 | 40.2 | 1 | 15.9 | 1.81 | 2.99 | 4.14 | 1.4 | 25600 | 1280 | 16.4 | 1220 | 153 | 3.58 | 79.4 | 449000 | 324 |  | Use: Cbo = | 0.715 |  | 1 | 0 | 0.67
|  |  |  | RL(min) = | -0.73088 | = -Pv*(Lo-S/2)/L+w/1000/(2*L)*(L^2-Lo^2) |  |  |  |  | Lateral Flange Bending Moment from Torsion for Simple-Span: |  |  |  |  | (per USS Steel Design Manual, 1981) |  |  |  |  | W40x321 | 94.1 | 40.08 | 1 | 15.91 | 1.77 | 2.9375 | 4.13 | 1.42 | 25100 | 1250 | 16.3 | 1190 | 150 | 3.56 | 79.4 | 446000 | 321 |  |  |  |  | 2 | 0.1 | 0.7
Parameters and Coefficients: | [10 empty] | e = | 6.1 | in. | e = d/2 (assume horiz. load taken at bot. flange) | [6 empty] | W40x298 | 87.6 | 39.69 | 0.83 | 17.83 | 1.575 | 3 | 4.7 | 1.41 | 24200 | 1220 | 16.6 | 1490 | 167 | 4.12 | 56.3 | 540000 | 298 |  |  |  |  | 3 | 0.2 | 0.73
Pv = | 7.4 | kips | Pv = P*(1+Vi/100)+Wt+Wh (vertical load) | [7 empty] | at = | 53.3545 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | [6 empty] | W40x297 | 87.4 | 39.8 | 0.93 | 15.8 | 1.65 | 2.83 | 4.11 | 1.53 | 23200 | 1170 | 16.3 | 1090 | 138 | 3.54 | 61.2 | 397000 | 297 |  |  |  |  | 4 | 0.3 | 0.76
Pw = | 1.85 | kips/wheel | Pw = Pv/Nw (load per trolley wheel) | [7 empty] | Mt = | 0.67375 | ft-kips | Mt = Ph*e*at/(2*(d-tf))*TANH(L*12/(2*at))/12 | [6 empty] | W40x278 | 81.8 | 40.2 | 1.02 | 12 | 1.81 | 2.99 | 3.02 | 1.85 | 20500 | 1020 | 15.8 | 521 | 87.1 | 2.52 | 64.7 | 192000 | 278 |  |  |  |  | 5 | 0.4 | 0.8
Ph = | 0.6 | kips | Ph = HLF*P (horizontal load) | [7 empty] | X-axis Stresses for Simple-Span: | [9 empty] | W40x277 | 81.4 | 39.7 | 0.83 | 15.8 | 1.58 | 2.76 | 4.13 | 1.59 | 21900 | 1100 | 16.4 | 1040 | 132 | 3.58 | 51.5 | 378000 | 277 |  |  |  |  | 6 | 0.5 | 0.84
ta = | 0.64 | in. | ta = tf (for W-shape) | [7 empty] | fbx = | 5.9595 | ksi | fbx = Mx/Sx | [6 empty] | W40x268 | 78.8 | 39.37 | 0.75 | 17.75 | 1.415 | 2.8125 | 4.67 | 1.57 | 21500 | 1090 | 16.5 | 1320 | 149 | 4.09 | 41.1 | 475000 | 268 |  |  |  |  | 7 | 0.6 | 0.9
l = | 0.097276 |  | l = 2*a/(bf-tw) | [7 empty] | Lc = | 8.5289 | ft. | Lc = Min. of: (76*bf/SQRT(Fy))/12 or (20000/(d/Af*Fy))/12 | [6 empty] | W40x264 | 77.6 | 40 | 0.96 | 11.9 | 1.73 | 2.91 | 3.01 | 1.94 | 19400 | 971 | 15.8 | 493 | 82.6 | 2.52 | 56.1 | 181000 | 264 |  |  |  |  | 8 | 0.7 | 0.96
Cxo = | -1.9033 |  | Cxo = -2.110+1.977*l+0.0076*e^(6.53*l) | [7 empty] | Lu = | 19.6171 | ft. | Lu = Max. of: (20000/(d/Af*Fy))/12 or (SQRT(102000/Fy)*rt)/12 | [6 empty] | W40x249 | 73.3 | 39.4 | 0.75 | 15.8 | 1.42 | 2.6 | 4.1 | 1.76 | 19600 | 993 | 16.3 | 926 | 118 | 3.55 | 38.1 | 334000 | 249 |  |  |  |  | 9 | 0.8 | 1.05
Cx1 = | 0.53539 |  | Cx1 = 10.108-7.408*l-10.108*e^(-1.364*l) | [7 empty] | Lb/rt = | 94.0092 |  | Lb/rt = Lb*12/rt | [6 empty] | W40x244 | 71.7 | 39.06 | 0.71 | 17.71 | 1.26 | 2.625 | 4.63 | 1.75 | 19200 | 983 | 16.4 | 1170 | 132 | 4.04 | 30.4 | 417000 | 244 |  |  |  |  | 10 | 0.9 | 1.15
Czo = | 0.19202 |  | Czo = 0.050-0.580*l+0.148*e^(3.015*l) | [7 empty] | fa/Fy = | 0 |  | fa/Fy = 0, as P(axial) is assumed = 0 | [6 empty] | W40x235 | 69 | 39.7 | 0.83 | 11.9 | 1.58 | 2.76 | 3.01 | 2.12 | 17400 | 875 | 15.9 | 444 | 74.6 | 2.54 | 41.3 | 161000 | 235 |  |  |  |  | 11 | 1 | 1.28
Cz1 = | 2.3187 |  | Cz1 = 2.230-1.490*l+1.390*e^(-18.33*l) | [7 empty] | Is Lb<=Lc? | No | [8 empty] | W40x221 | 64.8 | 38.67 | 0.71 | 17.71 | 1.065 | 2.4375 | 4.56 | 2.05 | 16600 | 858 | 16 | 988 | 112 | 3.9 | 21.2 | 349000 | 221 |  |  |  |  | 2 | 0.1 | 0.7
[11 empty] | Is d/tw<=allow? | Yes | [8 empty] | W40x215 | 63.4 | 39 | 0.65 | 15.8 | 1.22 | 2.4 | 4.09 | 2.03 | 16700 | 859 | 16.2 | 796 | 101 | 3.54 | 24.8 | 284000 | 215 |  |  |  |  | 3 | 0.2 | 0.73
Bending Moments for Simple-Span: | [10 empty] | Is b/t<=65/SQRT(Fy)? | Yes | [8 empty] | W40x211 | 62 | 39.4 | 0.75 | 11.8 | 1.42 | 2.6 | 2.98 | 2.36 | 15500 | 786 | 15.8 | 390 | 66.1 | 2.51 | 30.4 | 140000 | 211
x = | 8.3125 | ft. | x = 1/2*(L-S/2) (location of max. moments from left end of simple-span) | [7 empty] | Is b/t>95/SQRT(Fy)? | No |  |  |  |  | Note: the calculation below is only used as a comparison/check against the main calculation to the left. |  |  |  | W40x199 | 58.5 | 38.7 | 0.65 | 15.8 | 1.07 | 2.25 | 4.04 | 2.31 | 14900 | 770 | 16 | 695 | 88.2 | 3.45 | 18.3 | 246000 | 199
Mx = | 31.8832 | ft-kips | Mx = (Pv/2)/(2*L)*(L-S/2)^2+w/1000*x/2*(L-x) | [7 empty] | Fbx = | N.A. | Eqn. F1-1 | Fbx = 0.66*Fy |  |  | Torsion Analysis for Simple-Span per AISC Design Guide Series No. 9, Case 3: |  |  |  | W40x192 | 56.5 | 38.2 | 0.71 | 17.71 | 0.83 | 2.25 | 4.43 | 2.6 | 13500 | 708 | 15.5 | 770 | 87 | 3.69 | 13.7 | 268000 | 192
My = | 2.4387 | ft-kips | My = (Ph/2)/(2*L)*(L-S/2)^2 | [7 empty] | Fbx = | N.A. | Eqn. F1-3 | Fbx = Fy*(0.79-0.002*bf/(2*tf)*SQRT(Fy)) |  |  | e = | 6.1 | in. | e = d/2 | W40x183 | 53.8 | 39 | 0.65 | 11.8 | 1.22 | 2.4 | 2.98 | 2.71 | 13300 | 683 | 15.7 | 336 | 56.9 | 2.5 | 20 | 120000 | 183
[11 empty] | Fbx = | N.A. | Eqn. F1-5 | Fbx = 0.60*Fy |  |  | T = | 3.66 | in.-kips | T = Ph*e | W40x174 | 51.1 | 38.2 | 0.65 | 15.75 | 0.83 | 2 | 3.92 | 2.92 | 12200 | 639 | 15.5 | 541 | 68.8 | 3.26 | 11.2 | 189000 | 174
Lateral Flange Bending Moment from Torsion for Simple-Span: | [5 empty] | (per USS Steel Design Manual, 1981) |  |  |  |  | Fbx = | 16.5139 | Eqn. F1-6 | Fbx = (2/3-Fy*(Lb*12/rt)^2/(1530000*Cb)*Fy <= 0.60*Fy |  |  | at = | 53.3545 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | W40x167 | 49.2 | 38.6 | 0.65 | 11.8 | 1.02 | 2.21 | 2.91 | 3.19 | 11600 | 600 | 15.3 | 283 | 47.9 | 2.4 | 14 | 99800 | 167
e = | 6.1 | in. | e = d/2 (assume horiz. load taken at bot. flange) | [7 empty] | Fbx = | N.A. | Eqn. F1-7 | Fbx = 170000*Cb/(Lb*12/rt)^2 <= 0.60*Fy |  |  | Wns = | 23.3512 | in.^2 | Wns = (d-tf)*bf/4 | W40x149 | 43.8 | 38.2 | 0.63 | 11.8 | 0.83 | 2.01 | 2.84 | 3.9 | 9800 | 513 | 15 | 229 | 38.8 | 2.29 | 9.36 | 80000 | 149
at = | 53.3545 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | [7 empty] | Fbx = | 21.6 | Eqn. F1-8 | Fbx = 12000*Cb/(Lb*12*(d/Af)) <= 0.60*Fy |  |  | a = | 0.5 |  | a = 0.500 (torque assumed at midspan) | W36x848 | 249 | 42.45 | 2.52 | 18.13 | 4.53 | 5.6875 | 4.84 | 0.52 | 67400 | 3170 | 16.4 | 4550 | 501 | 4.27 | 1270 | 1620000 | 848
Mt = | 0.67375 | ft-kips | Mt = Ph*e*at/(2*(d-tf))*TANH(L*12/(2*at))/12 | [7 empty] | Fbx = | 21.6 | Select from F1-6, F1-7, & F1-8 |  |  |  | z = | 102 | in. | z = L*12/2 (calculated at midspan) | W36x798 | 235 | 42 | 2.38 | 18 | 4.29 | 5.24 | 4.8 | 0.54 | 62600 | 2980 | 16.3 | 4200 | 467 | 4.23 | 1050 | 1490000 | 798
[11 empty] | Use: Fbx = | 21.6 | ksi |  |  |  | c1 = | 0.0001911 |  | c1 = T/(J*G) | W36x720 | 211 | 41.19 | 2.165 | 17.775 | 3.9 | 5.0625 | 4.73 | 0.59 | 55300 | 2690 | 16.2 | 3680 | 414 | 4.18 | 804 | 1270000 | 720
X-axis Stresses for Simple-Span: | [10 empty] | Y-axis Stresses for Simple-Span: | [5 empty] | c2 = | -0.14466 |  | c2 = SINH(a*L*12/at)/TANH(L*12/at)-COSH(a*L*12/at) | W36x650 | 191 | 40.5 | 1.97 | 17.6 | 3.54 | 4.49 | 4.67 | 0.65 | 48900 | 2420 | 16 | 3230 | 367 | 4.11 | 591 | 1100000 | 650
fbx = | 5.9595 | ksi | fbx = Mx/Sx | [7 empty] | fby = | 2.1054 | ksi | fby = My/Sy |  |  | q'' = | -1.7143e-06 |  | q'' = c1*c2/at*SINH(z/at) | W36x588 | 172 | 39.84 | 1.79 | 17.4 | 3.23 | 4.375 | 4.62 | 0.71 | 43500 | 2180 | 15.9 | 2850 | 328 | 4.07 | 453 | 950000 | 588
Lb/rt = | 94.0092 |  | Lb/rt = Lb*12/rt | [7 empty] | fwns = | 1.1633 | ksi | fwns = Mt*12/(Sy/2) (warping normal stress) |  |  | sn = | 1.1609 | ksi | sn = ABS(E*Wns*q'') (warping normal stress) | W36x527 | 155 | 39.2 | 1.61 | 17.2 | 2.91 | 3.86 | 4.57 | 0.78 | 38300 | 1950 | 15.7 | 2490 | 289 | 4.01 | 327 | 820000 | 527
Fbx = | 21.6 | ksi | Fbx = 12000*Cb/(Lb*12*(d/Af)) <= 0.60*Fy | [5 empty] | fbx <= Fbx, O.K. |  | fby(total) = | 3.2687 | ksi | fby(total) = fby+fwns | [6 empty] | W36x485 | 142 | 38.74 | 1.5 | 17.105 | 2.68 | 3.8125 | 4.53 | 0.85 | 34700 | 1790 | 15.6 | 2250 | 263 | 3.98 | 260 | 727000 | 485 | SR = | 0.2759
[9 empty] | (continued) |  | Fby = | 27 | ksi | Fby = 0.75*Fy | [6 empty] | W36x439 | 129 | 38.3 | 1.36 | 17 | 2.44 | 3.39 | 4.49 | 0.92 | 31000 | 1620 | 15.5 | 1990 | 235 | 3.93 | 193 | 638000 | 439
[11 empty] | Combined Stress Ratio for Simple-Span: | [9 empty] | W36x393 | 116 | 37.8 | 1.22 | 16.8 | 2.2 | 3.15 | 4.45 | 1.02 | 27500 | 1450 | 15.4 | 1750 | 208 | 3.9 | 141 | 554000 | 393
Y-axis Stresses for Simple-Span: | [10 empty] | S.R. = | 0.39696 |  | S.R. = fbx/Fbx+fby(total)/Fby | [6 empty] | W36x359 | 105 | 37.4 | 1.12 | 16.7 | 2.01 | 2.96 | 4.42 | 1.11 | 24800 | 1320 | 15.3 | 1570 | 188 | 3.86 | 108 | 492000 | 359
fby = | 2.1054 | ksi | fby = My/Sy | [7 empty] | Vertical Deflection for Simple-Span: | [9 empty] | W36x328 | 96.4 | 37.1 | 1.02 | 16.6 | 1.85 | 2.8 | 4.39 | 1.21 | 22500 | 1210 | 15.3 | 1420 | 171 | 3.84 | 84.1 | 441000 | 328
fwns = | 1.1633 | ksi | fwns = Mt*12/(Sy/2) (warping normal stress) | [7 empty] | Pv = | 6.5 | kips | Pv = P+Wh+Wt (without vertical impact) | [6 empty] | W36x300 | 88.3 | 36.7 | 0.945 | 16.7 | 1.68 | 2.63 | 4.39 | 1.31 | 20300 | 1110 | 15.2 | 1300 | 156 | 3.83 | 64.2 | 399000 | 300
fby(total) = | 3.2687 | ksi | fby(total) = fby+fwns | [7 empty] | D(max) = | 0.10938 | in. | D(max) = | (Pv/2)*(L-S)/2/(24*E*I)*(3*L^2-4*((L-S)/2)^2)+5*w/12000*L^4/(384*E*I) | [5 empty] | W36x280 | 82.4 | 36.5 | 0.885 | 16.6 | 1.57 | 2.52 | 4.37 | 1.4 | 18900 | 1030 | 15.1 | 1200 | 144 | 3.81 | 52.6 | 366000 | 280
Fby = | 27 | ksi | Fby = 0.75*Fy | [5 empty] | fby <= Fby, O.K. |  | D(ratio) = | L/1865 |  | D(ratio) = L*12/D(max) | [6 empty] | W36x260 | 76.5 | 36.3 | 0.84 | 16.6 | 1.44 | 2.39 | 4.34 | 1.52 | 17300 | 953 | 15 | 1090 | 132 | 3.78 | 41.5 | 330000 | 260 | SR = | 0.12106
[11 empty] | D(allow) = | 0.45333 | in. | D(allow) = L*12/450 | [6 empty] | W36x256 | 75.4 | 37.4 | 0.96 | 12.2 | 1.73 | 2.48 | 3.14 | 1.77 | 16800 | 895 | 14.9 | 528 | 86.5 | 2.65 | 52.9 | 168000 | 256
Combined Stress Ratio for Simple-Span: | [10 empty] | Bending Moments for Overhang: | [9 empty] | W36x245 | 72.1 | 36.1 | 0.8 | 16.5 | 1.35 | 2.3 | 4.32 | 1.62 | 16100 | 895 | 15 | 1010 | 123 | 3.75 | 34.6 | 305000 | 245
S.R. = | 0.39696 |  | S.R. = fbx/Fbx+fby(total)/Fby | [5 empty] | S.R. <= 1.0, O.K. |  | Mx = | 19.65 | ft-kips | Mx = (Pv/2)*(Lo+(Lo-S))+w/1000*Lo^2/2 | [6 empty] | W36x232 | 68.1 | 37.1 | 0.87 | 12.1 | 1.57 | 2.32 | 3.11 | 1.95 | 15000 | 809 | 14.8 | 468 | 77.2 | 2.62 | 39.6 | 148000 | 232 | SR = | 0.39696
[11 empty] | My = | 1.575 | ft-kips | My = (Ph/2)*(Lo+(Lo-S)) | [6 empty] | W36x230 | 67.6 | 35.9 | 0.76 | 16.5 | 1.26 | 2.21 | 4.3 | 1.73 | 15000 | 837 | 14.9 | 940 | 114 | 3.73 | 28.6 | 282000 | 230
Vertical Deflection for Simple-Span: | [10 empty] | Lateral Flange Bending Moment from Torsion for Overhang: |  |  |  |  | (per USS Steel Design Manual, 1981) |  |  |  |  | W36x210 | 61.8 | 36.7 | 0.83 | 12.2 | 1.36 | 2.11 | 3.09 | 2.21 | 13200 | 719 | 14.6 | 411 | 67.5 | 2.58 | 28 | 128000 | 210
Pv = | 6.5 | kips | Pv = P+Wh+Wt (without vertical impact) | [7 empty] | e = | 6.1 | in. | e = d/2 (assume horiz. load taken at bot. flange) | [6 empty] | W36x194 | 57 | 36.5 | 0.765 | 12.1 | 1.26 | 2.01 | 3.07 | 2.39 | 12100 | 664 | 14.6 | 375 | 61.9 | 2.56 | 22.2 | 116000 | 194
D(max) = | 0.10938 | in. | D(max) = | (Pv/2)*(L-S)/2/(24*E*I)*(3*L^2-4*((L-S)/2)^2)+5*w/12000*L^4/(384*E*I) | [6 empty] | at = | 53.3545 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | [6 empty] | W36x182 | 53.6 | 36.3 | 0.725 | 12.1 | 1.18 | 1.93 | 3.05 | 2.55 | 11300 | 623 | 14.5 | 347 | 57.6 | 2.55 | 18.5 | 107000 | 182
D(ratio) = | L/1865 |  | D(ratio) = L*12/D(max) | [7 empty] | Mt = | 0.82785 | ft-kips | Mt = Ph*e*at/(d-tf)*TANH(Lo*12/at)/12 | [6 empty] | W36x170 | 50.1 | 36.2 | 0.68 | 12 | 1.1 | 1.85 | 3.04 | 2.73 | 10500 | 581 | 14.5 | 320 | 53.2 | 2.53 | 15.1 | 98400 | 170
D(allow) = | 0.45333 | in. | D(allow) = L*12/450 | [5 empty] | Defl.(max) <= Defl.(allow), O.K. |  | X-axis Stresses for Overhang: | [9 empty] | W36x160 | 47 | 36 | 0.65 | 12 | 1.02 | 1.77 | 3.02 | 2.94 | 9760 | 542 | 14.4 | 295 | 49.1 | 2.5 | 12.4 | 90300 | 160 | SR = | 0.24129
|  |  |  | (from CMAA Specification No. 74, Section 1.4.1.2) | [6 empty] | fbx = | 3.6729 | ksi | fbx = Mx/Sx | [6 empty] | W36x150 | 44.2 | 35.9 | 0.625 | 12 | 0.94 | 1.69 | 2.99 | 3.18 | 9040 | 504 | 14.3 | 270 | 45.1 | 2.47 | 10.1 | 82300 | 150
Bending Moments for Overhang: | [10 empty] | Lc = | 8.5289 | ft. | Lc = Min. of: (76*bf/SQRT(Fy))/12 or (20000/(d/Af*Fy))/12 | [6 empty] | W36x135 | 39.7 | 35.6 | 0.6 | 12 | 0.79 | 1.54 | 2.93 | 3.77 | 7800 | 439 | 14 | 225 | 37.7 | 2.38 | 7 | 68000 | 135
Mx = | 19.65 | ft-kips | Mx = (Pv/2)*(Lo+(Lo-S))+w/1000*Lo^2/2 | [7 empty] | Lu = | 19.6171 | ft. | Lu = Max. of: (20000/(d/Af*Fy))/12 or (SQRT(102000/Fy)*rt)/12 | [6 empty] | W33x619 | 181 | 38.47 | 1.97 | 16.91 | 3.54 | 4.375 | 4.51 | 0.64 | 41800 | 2170 | 15.2 | 2870 | 340 | 3.98 | 567 | 870000 | 619
My = | 1.575 | ft-kips | My = (Ph/2)*(Lo+(Lo-S)) | [7 empty] | Lbo/rt = | 63.5945 |  | Lbo/rt = Lbo*12/rt | [6 empty] | W33x567 | 166 | 37.91 | 1.81 | 16.75 | 3.27 | 4.0625 | 4.46 | 0.69 | 37700 | 1990 | 15.1 | 2580 | 308 | 3.94 | 444 | 768000 | 567
[11 empty] | fa/Fy = | 0 |  | fa/Fy = 0, as P(axial) is assumed = 0 | [6 empty] | W33x515 | 151 | 37.36 | 1.65 | 16.59 | 2.99 | 3.8125 | 4.42 | 0.75 | 33700 | 1810 | 14.9 | 2290 | 276 | 3.89 | 338 | 672000 | 515
Lateral Flange Bending Moment from Torsion for Overhang: | [5 empty] | (per USS Steel Design Manual, 1981) |  |  |  |  | Is Lbo<=Lc? | No | [8 empty] | W33x468 | 137 | 36.81 | 1.52 | 16.455 | 2.72 | 3.5 | 4.37 | 0.82 | 30100 | 1630 | 14.8 | 2030 | 247 | 3.85 | 256 | 587000 | 468
e = | 6.1 | in. | e = d/2 (assume horiz. load taken at bot. flange) | [7 empty] | Is d/tw<=allow? | Yes | [8 empty] | W33x424 | 124 | 36.34 | 1.38 | 16.315 | 2.48 | 3.3125 | 4.33 | 0.9 | 26900 | 1480 | 14.7 | 1800 | 221 | 3.81 | 193 | 514000 | 424
at = | 53.3545 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | [7 empty] | Is b/t<=65/SQRT(Fy)? | Yes | [8 empty] | W33x387 | 114 | 36 | 1.26 | 16.2 | 2.28 | 3.07 | 4.3 | 0.97 | 24300 | 1350 | 14.6 | 1620 | 200 | 3.77 | 148 | 459000 | 387
Mt = | 0.82785 | ft-kips | Mt = Ph*e*at/(d-tf)*TANH(Lo*12/at)/12 | [7 empty] | Is b/t>95/SQRT(Fy)? | No |  |  |  |  | Note: the calculation below is only used as a comparison/check against the main calculation to the left. |  |  |  | W33x354 | 104 | 35.6 | 1.16 | 16.1 | 2.09 | 2.88 | 4.27 | 1.06 | 22000 | 1240 | 14.5 | 1460 | 181 | 3.74 | 115 | 409000 | 354
[11 empty] | Fbx = | N.A. | Eqn. F1-1 | Fbx = 0.66*Fy |  |  | Torsion Analysis for Fixed-End Cantilever per AISC Design Guide Series No. 9, Case 9: |  |  |  | W33x318 | 93.6 | 35.2 | 1.04 | 16 | 1.89 | 2.68 | 4.24 | 1.16 | 19500 | 1110 | 14.5 | 1290 | 161 | 3.71 | 84.4 | 357000 | 318
X-axis Stresses for Overhang: | [10 empty] | Fbx = | N.A. | Eqn. F1-3 | Fbx = Fy*(0.79-0.002*bf/(2*tf)*SQRT(Fy)) |  |  | e = | 6.1 | in. | e = d/2 | W33x291 | 85.7 | 34.8 | 0.96 | 15.9 | 1.73 | 2.52 | 4.21 | 1.27 | 17700 | 1020 | 14.4 | 1160 | 146 | 3.68 | 65.1 | 318000 | 291
fbx = | 3.6729 | ksi | fbx = Mx/Sx | [7 empty] | Fbx = | N.A. | Eqn. F1-5 | Fbx = 0.60*Fy |  |  | T = | 3.66 | in.-kips | T = Ph*e | W33x263 | 77.5 | 34.5 | 0.87 | 15.8 | 1.57 | 2.36 | 4.18 | 1.39 | 15900 | 919 | 14.3 | 1040 | 131 | 3.66 | 48.7 | 282000 | 263
Lbo/rt = | 63.5945 |  | Lbo/rt = Lbo*12/rt | [7 empty] | Fbx = | 20.5743 | Eqn. F1-6 | Fbx = (2/3-Fy*(Lbo*12/rt)^2/(1530000*Cbo)*Fy <= 0.60*Fy |  |  | at = | 53.3545 |  | at = SQRT(E*Cw/(J*G)) , E=29000 ksi and G=11200 ksi | W33x241 | 71 | 34.2 | 0.83 | 15.9 | 1.4 | 2.19 | 4.17 | 1.54 | 14200 | 831 | 14.1 | 933 | 118 | 3.62 | 36.2 | 251000 | 241
Fbx = | 21.6 | ksi | Fbx = 12000*Cbo/(Lbo*12*(d/Af)) <= 0.60*Fy |  |  |  |  | fbx <= Fbx, O.K. |  |  | Fbx = | N.A. | Eqn. F1-7 | Fbx = 170000*Cbo/(Lbo*12/rt)^2 <= 0.60*Fy |  |  | Wns = | 23.3512 | in.^2 | Wns = (d-tf)*bf/4 | W33x221 | 65.2 | 33.9 | 0.775 | 15.8 | 1.27 | 2.06 | 4.15 | 1.68 | 12900 | 759 | 14.1 | 840 | 106 | 3.59 | 27.8 | 224000 | 221 | SR = | 0.17004
[11 empty] | Fbx = | 21.6 | Eqn. F1-8 | Fbx = 12000*Cbo/(Lbo*12*(d/Af)) <= 0.60*Fy |  |  | a = | 1 |  | a = 1.000 (torque assumed at free end of cantilever) | W33x201 | 59.2 | 33.7 | 0.715 | 15.7 | 1.15 | 1.94 | 4.12 | 1.86 | 11600 | 686 | 14 | 749 | 95.2 | 3.56 | 20.8 | 198000 | 201
Y-axis Stresses for Overhang: | [10 empty] | Fbx = | 21.6 | Select from F1-6, F1-7, & F1-8 |  |  |  | z = | 0 | in. | z = Lo*12 (calculated at fixed end of cantilever) | W33x169 | 49.5 | 33.8 | 0.67 | 11.5 | 1.22 | 1.92 | 2.95 | 2.41 | 9290 | 549 | 13.7 | 310 | 53.9 | 2.5 | 17.7 | 82400 | 169
fby = | 1.3597 | ksi | fby = My/Sy | [7 empty] | Use: Fbx = | 21.6 | ksi |  |  |  | c1 = | 0.0001911 |  | c1 = T/(J*G) | W33x152 | 44.8 | 33.5 | 0.635 | 11.6 | 1.06 | 1.76 | 2.94 | 2.74 | 8160 | 487 | 13.5 | 273 | 47.2 | 2.47 | 12.4 | 71800 | 152
fwns = | 1.4294 | ksi | fwns = Mt*12/(Sy/2) (warping normal stress) | [7 empty] | Y-axis Stresses for Overhang: | [5 empty] | c2 = | 0.58808 |  | c2 = SINH(a*Lo*12/at)-TANH(Lo*12/at)*COSH(a*Lo*12/at)+TANH(Lo*12/at) | W33x141 | 41.6 | 33.3 | 0.605 | 11.5 | 0.96 | 1.66 | 2.92 | 3.01 | 7450 | 448 | 13.4 | 246 | 42.7 | 2.43 | 9.7 | 64300 | 141
fby(total) = | 2.7891 | ksi | fby(total) = fby+fwns | [7 empty] | fby = | 1.3597 | ksi | fby = My/Sy |  |  | q'' = | 2.1064e-06 |  | q'' = c1/at*(c2*COSH(z/at)-SINH(z/at)) | W33x130 | 38.3 | 33.1 | 0.58 | 11.5 | 0.855 | 1.56 | 2.88 | 3.36 | 6710 | 406 | 13.2 | 218 | 37.9 | 2.39 | 7.37 | 56600 | 130
Fby = | 27 | ksi | Fby = 0.75*Fy |  |  |  |  | fby <= Fby, O.K. |  |  | fwns = | 1.4294 | ksi | fwns = Mt*12/(Sy/2) (warping normal stress) |  |  | sn = | 1.4264 | ksi | sn = ABS(E*Wns*q'') (warping normal stress) | W33x118 | 34.7 | 32.9 | 0.55 | 11.5 | 0.74 | 1.44 | 2.84 | 3.87 | 5900 | 359 | 13 | 187 | 32.6 | 2.32 | 5.3 | 48200 | 118 | SR = | 0.1033
[11 empty] | fby(total) = | 2.7891 | ksi | fby(total) = fby+fwns | [6 empty] | W30x581 | 170 | 35.39 | 1.97 | 16.2 | 3.54 | 4.3125 | 4.34 | 0.62 | 33000 | 1870 | 13.9 | 2530 | 312 | 3.86 | 537 | 636000 | 581
Combined Stress Ratio for Overhang: | [10 empty] | Fby = | 27 | ksi | Fby = 0.75*Fy | [6 empty] | W30x526 | 154 | 34.76 | 1.79 | 16.02 | 3.23 | 4 | 4.29 | 0.67 | 29300 | 1680 | 13.8 | 2230 | 278 | 3.8 | 405 | 550000 | 526
S.R. = | 0.27334 |  | S.R. = fbx/Fbx+fby(total)/Fby |  |  |  |  | S.R. <= 1.0, O.K. |  |  | Combined Stress Ratio for Overhang: | [9 empty] | W30x477 | 140 | 34.21 | 1.63 | 15.865 | 2.95 | 3.75 | 4.24 | 0.73 | 26100 | 1530 | 13.7 | 1970 | 249 | 3.75 | 307 | 480000 | 477 | SR = | 0.27334
[11 empty] | S.R. = | 0.27334 |  | S.R. = fbx/Fbx+fby(total)/Fby | [6 empty] | W30x433 | 127 | 33.66 | 1.5 | 15.725 | 2.68 | 3.4375 | 4.2 | 0.8 | 23200 | 1380 | 13.5 | 1750 | 222 | 3.71 | 231 | 417000 | 433
Vertical Deflection for Overhang: |  |  | (for Nw = 4 and S < Lo, assume all of Pv without impact at end of overhang) | [7 empty] | Vertical Deflection for Overhang: |  |  | (for Nw = 4 and S < Lo, assume all of Pv without impact at end of overhang) | [6 empty] | W30x391 | 115 | 33.2 | 1.36 | 15.6 | 2.44 | 3.23 | 4.16 | 0.87 | 20700 | 1250 | 13.4 | 1550 | 198 | 3.67 | 173 | 366000 | 391
Pv = | 6.5 | kips | Pv = P+Wh+Wt (without vertical impact) | [7 empty] | Pv = | 6.5 | kips | Pv = P+Wh+Wt (without vertical impact) | [6 empty] | W30x357 | 105 | 32.8 | 1.24 | 15.5 | 2.24 | 3.03 | 4.12 | 0.95 | 18700 | 1140 | 13.3 | 1390 | 179 | 3.64 | 134 | 325000 | 357
D(max) = | 0.055414 | in. | D(max) = | Pv*Lo^2*(L+Lo)/(3*E*I)+w/12000*Lo*(4*Lo^2*L-L^3+3*Lo^3)/(24*E*I) | [6 empty] | D(max) = | 0.055414 | in. | D(max) = | Pv*Lo^2*(L+Lo)/(3*E*I)+w/12000*Lo*(4*Lo^2*L-L^3+3*Lo^3)/(24*E*I) | [5 empty] | W30x326 | 95.8 | 32.4 | 1.14 | 15.4 | 2.05 | 2.84 | 4.09 | 1.03 | 16800 | 1040 | 13.2 | 1240 | 162 | 3.6 | 103 | 286000 | 326
D(ratio) = | L/650 |  | D(ratio) = Lo*12/D(max) | [7 empty] | D(ratio) = | L/650 |  | D(ratio) = Lo*12/D(max) | [6 empty] | W30x292 | 85.9 | 32 | 1.02 | 15.3 | 1.85 | 2.64 | 4.06 | 1.13 | 14900 | 930 | 13.2 | 1100 | 144 | 3.58 | 75.2 | 250000 | 292
D(allow) = | 0.08 | in. | D(allow) = Lo*12/450 | [5 empty] | Defl.(max) <= Defl.(allow), O.K. |  | D(allow) = | 0.08 | in. | D(allow) = Lo*12/450 | [6 empty] | W30x261 | 76.9 | 31.6 | 0.93 | 15.2 | 1.65 | 2.44 | 4.02 | 1.26 | 13100 | 829 | 13.1 | 959 | 127 | 3.53 | 54.1 | 215000 | 261 | SR = | 0.69268
[14 empty] | Notes: Values of "L", "Lo", & "S" in equation above for D(max) are multiplied by 12. | [6 empty] | W30x235 | 69.2 | 31.3 | 0.83 | 15.1 | 1.5 | 2.29 | 4 | 1.39 | 11700 | 748 | 13 | 855 | 114 | 3.51 | 40.3 | 190000 | 235
Bottom Flange Bending (simplified): | [10 empty] | Bottom Flange Bending (simplified): | [9 empty] | W30x211 | 62.2 | 30.9 | 0.775 | 15.1 | 1.32 | 2.1 | 3.99 | 1.56 | 10300 | 665 | 12.9 | 757 | 100 | 3.49 | 28.4 | 166000 | 211
be = | 7.68 | in. | Min. of: be = 12*tf or S*12 (effective flange bending length) | [7 empty] | be = | 7.68 | in. | Min. of: be = 12*tf or S*12 (effective flange bending length) | [6 empty] | W30x191 | 56.3 | 30.7 | 0.71 | 15 | 1.19 | 1.97 | 3.97 | 1.72 | 9200 | 600 | 12.8 | 673 | 89.5 | 3.46 | 21 | 146000 | 191
am = | 3.355 | in. | am = (bf/2-tw/2)-(k-tf) (where: k-tf = radius of fillet) | [7 empty] | tf2 = | 0.64 | in. | tf2 = tf (for W-shape) | [6 empty] | W30x173 | 51 | 30.4 | 0.655 | 15 | 1.07 | 1.85 | 3.94 | 1.91 | 8230 | 541 | 12.7 | 598 | 79.8 | 3.42 | 15.6 | 129000 | 173
Mf = | 5.513 | in.-kips | Mf = Pw*(am-a) | [7 empty] | am = | 3.355 | in. | am = (bf/2-tw/2)-(k-tf) (where: k-tf = radius of fillet) | [6 empty] | W30x148 | 43.5 | 30.7 | 0.65 | 10.5 | 1.18 | 1.83 | 2.7 | 2.48 | 6680 | 436 | 12.4 | 227 | 43.3 | 2.28 | 14.5 | 49400 | 148
Sf = | 0.52429 | in.^3 | Sf = be*tf^2/6 | [7 empty] | Mf = | 5.513 | in.-kips | Mf = Pw*(am-a) | [6 empty] | W30x132 | 38.9 | 30.3 | 0.615 | 10.5 | 1 | 1.65 | 2.68 | 2.87 | 5770 | 380 | 12.2 | 196 | 37.2 | 2.25 | 9.72 | 42100 | 132
fb = | 10.5152 | ksi | fb = Mf/Sf | [7 empty] | Sf = | 0.52429 | in.^3 | Sf = be*tf^2/6 | [6 empty] | W30x124 | 36.5 | 30.2 | 0.585 | 10.5 | 0.93 | 1.58 | 2.66 | 3.09 | 5360 | 355 | 12.1 | 181 | 34.4 | 2.23 | 7.99 | 38700 | 124
Fb = | 27 | ksi | Fb = 0.75*Fy | [5 empty] | fb <= Fb, O.K. |  | fb = | 10.5152 | ksi | fb = Mf/Sf | [6 empty] | W30x116 | 34.2 | 30 | 0.565 | 10.5 | 0.85 | 1.5 | 2.64 | 3.36 | 4930 | 329 | 12 | 164 | 31.3 | 2.19 | 6.43 | 34900 | 116 | SR = | 0.38945
[11 empty] | Fb = | 27 | ksi | Fb = 0.75*Fy | [6 empty] | W30x108 | 31.7 | 29.8 | 0.545 | 10.5 | 0.76 | 1.41 | 2.61 | 3.75 | 4470 | 299 | 11.9 | 146 | 27.9 | 2.15 | 4.99 | 30800 | 108
[11 empty] | Bottom Flange Bending per CMAA Specification No. 74 (2004): |  |  |  |  | (Note: torsion is neglected) |  |  |  |  | W30x99 | 29.1 | 29.7 | 0.52 | 10.5 | 0.67 | 1.32 | 2.57 | 4.23 | 3990 | 269 | 11.7 | 128 | 24.5 | 2.1 | 3.77 | 26900 | 99
[9 empty] | (continued) |  | Local Flange Bending Stress @ Point 0: |  |  |  |  | (Sign convention: + = tension, - = compression) |  |  |  |  | W30x90 | 26.4 | 29.5 | 0.47 | 10.4 | 0.61 | 1.26 | 2.56 | 4.65 | 3610 | 245 | 11.7 | 115 | 22.1 | 2.09 | 2.84 | 24000 | 90
[11 empty] | sxo = | -8.5966 | ksi | sxo = Cxo*Pw/ta^2 | [6 empty] | W27x539 | 159 | 32.5 | 1.97 | 15.3 | 3.54 | 4.33 | 4.1 | 0.6 | 25600 | 1570 | 12.7 | 2110 | 277 | 3.65 | 496 | 443000 | 539
Bottom Flange Bending per CMAA Specification No. 74 (2004): | [5 empty] | (Note: torsion is neglected) |  |  |  |  | szo = | 0.86729 | ksi | szo = Czo*Pw/ta^2 | [6 empty] | W27x494 | 145 | 31.97 | 1.81 | 15.095 | 3.27 | 4 | 4.05 | 0.65 | 22900 | 1440 | 12.6 | 1890 | 250 | 3.61 | 391 | 386000 | 494
[11 empty] | Local Flange Bending Stress @ Point 1: | [9 empty] | W27x448 | 131 | 31.42 | 1.65 | 14.94 | 2.99 | 3.6875 | 4.01 | 0.7 | 20400 | 1300 | 12.5 | 1670 | 224 | 3.57 | 297 | 336000 | 448
Local Flange Bending Stress @ Point 0: | [8 empty] | (Sign convention: + = tension, - = compression) |  | sx1 = | 2.4181 | ksi | sx1 = Cx1*Pw/ta^2 | [6 empty] | W27x407 | 119 | 30.87 | 1.52 | 14.8 | 2.72 | 3.4375 | 3.96 | 0.77 | 18100 | 1170 | 12.3 | 1480 | 200 | 3.52 | 225 | 291000 | 407
sxo = | -8.5966 | ksi | sxo = Cxo*Pw/ta^2 | [7 empty] | sz1 = | 10.4729 | ksi | sz1 = Cz1*Pw/ta^2 | [6 empty] | W27x368 | 108 | 30.4 | 1.38 | 14.7 | 2.48 | 3.27 | 3.93 | 0.84 | 16200 | 1060 | 12.2 | 1310 | 179 | 3.48 | 170 | 255000 | 368
szo = | 0.86729 | ksi | szo = Czo*Pw/ta^2 | [7 empty] | Local Flange Bending Stress @ Point 2: | [9 empty] | W27x336 | 98.9 | 30 | 1.26 | 14.6 | 2.28 | 3.07 | 3.89 | 0.9 | 14600 | 972 | 12.1 | 1180 | 162 | 3.45 | 131 | 227000 | 336
Local Flange Bending Stress @ Point 1: | [10 empty] | sx2 = | 8.5966 | ksi | sx2 = -sxo | [6 empty] | W27x307 | 90.4 | 29.6 | 1.16 | 14.4 | 2.09 | 2.88 | 3.86 | 0.98 | 13100 | 887 | 12 | 1050 | 146 | 3.41 | 101 | 199000 | 307
sx1 = | 2.4181 | ksi | sx1 = Cx1*Pw/ta^2 | [7 empty] | sz2 = | -0.86729 | ksi | sz2 = -szo | [6 empty] | W27x281 | 82.9 | 29.3 | 1.06 | 14.4 | 1.93 | 2.72 | 3.84 | 1.06 | 11900 | 814 | 12 | 953 | 133 | 3.39 | 79.5 | 178000 | 281
sz1 = | 10.4729 | ksi | sz1 = Cz1*Pw/ta^2 | [7 empty] | Resultant Biaxial Stress @ Point 0: | [9 empty] | W27x258 | 76 | 29 | 0.98 | 14.3 | 1.77 | 2.56 | 3.81 | 1.15 | 10800 | 745 | 11.9 | 859 | 120 | 3.36 | 61.6 | 159000 | 258
Local Flange Bending Stress @ Point 2: | [10 empty] | fbxo = | 5.9595 | ksi | fbxo = Mx*(d/2)/Ix = Mx/Sx | [6 empty] | W27x235 | 69.4 | 28.7 | 0.91 | 14.2 | 1.61 | 2.4 | 3.78 | 1.25 | 9700 | 677 | 11.8 | 769 | 108 | 3.33 | 47 | 141000 | 235
sx2 = | 8.5966 | ksi | sx2 = -sxo | [7 empty] | fbyo = | 0.096163 | ksi | fbyo = My*(tw/2)/Iy | [6 empty] | W27x217 | 64 | 28.4 | 0.83 | 14.1 | 1.5 | 2.29 | 3.76 | 1.34 | 8910 | 627 | 11.8 | 704 | 99.8 | 3.32 | 37.6 | 128000 | 217
sz2 = | -0.86729 | ksi | sz2 = -szo | [7 empty] | sz = | 6.7061 | ksi | sz = fbxo+fbyo+0.75*szo | [6 empty] | W27x194 | 57.2 | 28.1 | 0.75 | 14 | 1.34 | 2.13 | 3.74 | 1.49 | 7860 | 559 | 11.7 | 619 | 88.1 | 3.29 | 27.1 | 111000 | 194
Resultant Biaxial Stress @ Point 0: | [10 empty] | sx = | -6.4475 | ksi | sx = 0.75*sxo | [6 empty] | W27x178 | 52.5 | 27.8 | 0.725 | 14.1 | 1.19 | 1.98 | 3.72 | 1.66 | 7020 | 505 | 11.6 | 555 | 78.8 | 3.25 | 20.1 | 98300 | 178
fbxo = | 5.9595 |  | fbxo = Mx*(d/2)/Ix = Mx/Sx | [7 empty] | txz = | 0 | ksi | txz = 0 (assumed negligible) | [6 empty] | W27x161 | 47.6 | 27.6 | 0.66 | 14 | 1.08 | 1.87 | 3.7 | 1.82 | 6310 | 458 | 11.5 | 497 | 70.9 | 3.23 | 15.1 | 87300 | 161
fbyo = | 0.096163 |  | fbyo = My*(tw/2)/Iy | [7 empty] | sto = | 11.3921 | ksi | sto = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [6 empty] | W27x146 | 43.1 | 27.4 | 0.605 | 14 | 0.975 | 1.76 | 3.68 | 2.01 | 5660 | 414 | 11.5 | 443 | 63.5 | 3.2 | 11.3 | 77200 | 146
sz = | 6.7061 | ksi | sz = fbxo+fbyo+0.75*szo | [7 empty] | Resultant Biaxial Stress @ Point 1: | [9 empty] | W27x129 | 37.8 | 27.6 | 0.61 | 10 | 1.1 | 1.7 | 2.59 | 2.51 | 4760 | 345 | 11.2 | 184 | 36.8 | 2.21 | 11.1 | 32400 | 129
sx = | -6.4475 | ksi | sx = 0.75*sxo | [7 empty] | fbx1 = | 5.9595 | ksi | fbx1 = Mx*(d/2)/Ix = Mx/Sx | [6 empty] | W27x114 | 33.5 | 27.3 | 0.57 | 10.1 | 0.93 | 1.53 | 2.58 | 2.91 | 4080 | 299 | 11 | 159 | 31.5 | 2.18 | 7.33 | 27600 | 114
txz = | 0 | ksi | txz = 0 (assumed negligible) | [7 empty] | fby1 = | 1.9051 | ksi | fby1 = My*(bf/2-a)/Iy | [6 empty] | W27x102 | 30 | 27.1 | 0.515 | 10 | 0.83 | 1.43 | 2.56 | 3.26 | 3620 | 267 | 11 | 139 | 27.8 | 2.15 | 5.28 | 24000 | 102
sto = | 11.3921 | ksi | sto = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [5 empty] | <= Fb = 0.66*Fy = 23.76 ksi, O.K. |  | sz = | 15.7192 | ksi | sz = fbx1+fby1+0.75*sz1 | [6 empty] | W27x94 | 27.7 | 26.9 | 0.49 | 9.99 | 0.745 | 1.34 | 2.53 | 3.62 | 3270 | 243 | 10.9 | 124 | 24.8 | 2.12 | 4.03 | 21200 | 94 | SR = | 0.47946
Resultant Biaxial Stress @ Point 1: | [10 empty] | sx = | 1.8136 | ksi | sx = 0.75*sx1 | [6 empty] | W27x84 | 24.8 | 26.7 | 0.46 | 9.96 | 0.64 | 1.24 | 2.49 | 4.19 | 2850 | 213 | 10.7 | 106 | 21.2 | 2.07 | 2.81 | 18000 | 84
fbx1 = | 5.9595 |  | fbx1 = Mx*(d/2)/Ix = Mx/Sx | [7 empty] | txz = | 0 | ksi | txz = 0 (assumed negligible) | [6 empty] | W24x492 | 144 | 29.65 | 1.97 | 14.115 | 3.54 | 4.3125 | 3.8 | 0.59 | 19100 | 1290 | 11.5 | 1670 | 237 | 3.41 | 456 | 283000 | 492
fby1 = | 1.9051 |  | fby1 = My*(bf/2-a)/Iy | [7 empty] | st1 = | 14.8954 | ksi | st1 = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [6 empty] | W24x450 | 132 | 29.09 | 1.81 | 13.955 | 3.27 | 4.0625 | 3.76 | 0.64 | 17100 | 1170 | 11.4 | 1490 | 214 | 3.36 | 357 | 247000 | 450
sz = | 15.7192 | ksi | sz = fbx1+fby1+0.75*sz1 | [7 empty] | Resultant Biaxial Stress @ Point 2: | [9 empty] | W24x408 | 119 | 28.54 | 1.65 | 13.8 | 2.99 | 3.75 | 3.71 | 0.69 | 15100 | 1060 | 11.3 | 1320 | 191 | 3.33 | 271 | 214000 | 408
sx = | 1.8136 | ksi | sx = 0.75*sx1 | [7 empty] | fbx2 = | 5.3427 | ksi | fbx2 = Mx*(d/2-tf)/Ix | [6 empty] | W24x370 | 109 | 28 | 1.52 | 13.7 | 2.72 | 3.22 | 3.67 | 0.75 | 13400 | 957 | 11.1 | 1160 | 170 | 3.27 | 201 | 185000 | 370
txz = | 0 | ksi | txz = 0 (assumed negligible) | [7 empty] | fby2 = | 0.096163 | ksi | fby2 = My*(tw/2)/Iy | [6 empty] | W24x335 | 98.4 | 27.5 | 1.38 | 13.5 | 2.48 | 2.98 | 3.63 | 0.82 | 11900 | 864 | 11 | 1030 | 152 | 3.23 | 152 | 161000 | 335
st1 = | 14.8954 | ksi | st1 = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [5 empty] | <= Fb = 0.66*Fy = 23.76 ksi, O.K. |  | sz = | 4.7884 | ksi | sz = fbx2+fby2+0.75*sz2 | [6 empty] | W24x306 | 89.8 | 27.1 | 1.26 | 13.4 | 2.28 | 2.78 | 3.6 | 0.89 | 10700 | 789 | 10.9 | 919 | 137 | 3.2 | 117 | 142000 | 306 | SR = | 0.62691
Resultant Biaxial Stress @ Point 2: | [10 empty] | sx = | 6.4475 | ksi | sx = 0.75*sx2 | [6 empty] | W24x279 | 82 | 26.7 | 1.16 | 13.3 | 2.09 | 2.59 | 3.57 | 0.96 | 9600 | 718 | 10.8 | 823 | 124 | 3.17 | 90.5 | 125000 | 279
fbx2 = | 5.3427 |  | fbx2 = Mx*(d/2-tf)/Ix | [7 empty] | txz = | 0 | ksi | txz = 0 (assumed negligible) | [6 empty] | W24x250 | 73.5 | 26.3 | 1.04 | 13.2 | 1.89 | 2.39 | 3.53 | 1.06 | 8490 | 644 | 10.7 | 724 | 110 | 3.14 | 66.6 | 108000 | 250
fby2 = | 0.096163 |  | fby2 = My*(tw/2)/Iy | [7 empty] | st2 = | 5.7988 | ksi | st2 = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [6 empty] | W24x229 | 67.2 | 26 | 0.96 | 13.1 | 1.73 | 2.23 | 3.51 | 1.15 | 7650 | 588 | 10.7 | 651 | 99.4 | 3.11 | 51.3 | 96000 | 229
sz = | 4.7884 | ksi | sz = fbx2+fby2+0.75*sz2 | [17 empty] | W24x207 | 60.7 | 25.7 | 0.87 | 13 | 1.57 | 2.07 | 3.48 | 1.26 | 6820 | 531 | 10.6 | 578 | 88.8 | 3.08 | 38.3 | 84200 | 207
sx = | 6.4475 | ksi | sx = 0.75*sx2 | [17 empty] | W24x192 | 56.3 | 25.5 | 0.81 | 13 | 1.46 | 1.96 | 3.46 | 1.35 | 6260 | 491 | 10.5 | 530 | 81.8 | 3.07 | 30.8 | 76400 | 192
txz = | 0 | ksi | txz = 0 (assumed negligible) | [17 empty] | W24x176 | 51.7 | 25.2 | 0.75 | 12.9 | 1.34 | 1.84 | 3.44 | 1.46 | 5680 | 450 | 10.5 | 479 | 74.3 | 3.04 | 23.9 | 68400 | 176
st2 = | 5.7988 | ksi | st2 = SQRT(sx^2+sz^2-sx*sz+3*txz^2) | [5 empty] | <= Fb = 0.66*Fy = 23.76 ksi, O.K. | [11 empty] | W24x162 | 47.7 | 25 | 0.705 | 13 | 1.22 | 1.72 | 3.45 | 1.58 | 5170 | 414 | 10.4 | 443 | 68.4 | 3.05 | 18.5 | 62600 | 162 | SR = | 0.24406
[21 empty] | W24x146 | 43 | 24.7 | 0.65 | 12.9 | 1.09 | 1.59 | 3.43 | 1.76 | 4580 | 371 | 10.3 | 391 | 60.5 | 3.01 | 13.4 | 54700 | 146
[21 empty] | W24x131 | 38.5 | 24.5 | 0.605 | 12.9 | 0.96 | 1.46 | 3.4 | 1.98 | 4020 | 329 | 10.2 | 340 | 53 | 2.97 | 9.5 | 47000 | 131
[21 empty] | W24x117 | 34.4 | 24.3 | 0.55 | 12.8 | 0.85 | 1.35 | 3.37 | 2.23 | 3540 | 291 | 10.1 | 297 | 46.5 | 2.94 | 6.72 | 40700 | 117
[21 empty] | W24x104 | 30.6 | 24.1 | 0.5 | 12.8 | 0.75 | 1.25 | 3.35 | 2.52 | 3100 | 258 | 10.1 | 259 | 40.7 | 2.91 | 4.72 | 35200 | 104
[21 empty] | W24x103 | 30.3 | 24.5 | 0.55 | 9 | 0.98 | 1.48 | 2.33 | 2.78 | 3000 | 245 | 9.96 | 119 | 26.5 | 1.99 | 7.07 | 16500 | 103
[21 empty] | W24x94 | 27.7 | 24.3 | 0.515 | 9.07 | 0.875 | 1.38 | 2.33 | 3.06 | 2700 | 222 | 9.87 | 109 | 24 | 1.98 | 5.26 | 15000 | 94
[21 empty] | W24x84 | 24.7 | 24.1 | 0.47 | 9.02 | 0.77 | 1.27 | 2.31 | 3.47 | 2370 | 196 | 9.79 | 94.4 | 20.9 | 1.95 | 3.7 | 12800 | 84
[21 empty] | W24x76 | 22.4 | 23.9 | 0.44 | 8.99 | 0.68 | 1.18 | 2.29 | 3.91 | 2100 | 176 | 9.69 | 82.5 | 18.4 | 1.92 | 2.68 | 11100 | 76
[21 empty] | W24x68 | 20.1 | 23.7 | 0.415 | 8.97 | 0.585 | 1.09 | 2.26 | 4.52 | 1830 | 154 | 9.55 | 70.4 | 15.7 | 1.87 | 1.87 | 9430 | 68
[21 empty] | W24x62 | 18.3 | 23.7 | 0.43 | 7.04 | 0.59 | 1.19 | 1.71 | 5.72 | 1560 | 132 | 9.24 | 34.5 | 9.8 | 1.37 | 1.77 | 4620 | 62
[21 empty] | W24x55 | 16.3 | 23.6 | 0.395 | 7.01 | 0.505 | 1.11 | 1.68 | 6.66 | 1360 | 115 | 9.13 | 29.1 | 8.3 | 1.34 | 1.24 | 3870 | 55
[21 empty] | W21x402 | 118 | 26.02 | 1.73 | 13.405 | 3.13 | 3.875 | 3.63 | 0.62 | 12200 | 937 | 10.2 | 1270 | 189 | 3.27 | 297 | 165000 | 402
[21 empty] | W21x364 | 107 | 25.47 | 1.59 | 13.265 | 2.85 | 3.625 | 3.59 | 0.67 | 10800 | 846 | 10 | 1120 | 168 | 3.23 | 225 | 142000 | 364
[21 empty] | W21x333 | 97.9 | 25 | 1.46 | 13.13 | 2.62 | 3.375 | 3.55 | 0.73 | 9610 | 769 | 9.91 | 994 | 151 | 3.19 | 174 | 124000 | 333
[21 empty] | W21x300 | 88.2 | 24.53 | 1.32 | 12.99 | 2.38 | 3.125 | 3.51 | 0.78 | 8480 | 692 | 9.81 | 873 | 134 | 3.15 | 130 | 107000 | 300
[21 empty] | W21x275 | 80.8 | 24.13 | 1.22 | 12.89 | 2.19 | 3 | 3.48 | 0.85 | 7620 | 632 | 9.71 | 785 | 122 | 3.12 | 101 | 94100 | 275
[21 empty] | W21x248 | 72.8 | 23.74 | 1.1 | 12.775 | 1.99 | 2.75 | 3.45 | 0.94 | 6760 | 569 | 9.63 | 694 | 109 | 3.09 | 75.2 | 81800 | 248
[21 empty] | W21x223 | 65.4 | 23.35 | 1 | 12.675 | 1.79 | 2.5625 | 3.41 | 1.02 | 5950 | 510 | 9.54 | 609 | 96.1 | 3.05 | 54.9 | 70600 | 223
[21 empty] | W21x201 | 59.2 | 23 | 0.91 | 12.6 | 1.63 | 2.13 | 3.38 | 1.12 | 5310 | 461 | 9.47 | 542 | 86.1 | 3.02 | 40.9 | 62100 | 201
[21 empty] | W21x182 | 53.6 | 22.7 | 0.83 | 12.5 | 1.48 | 1.98 | 3.36 | 1.23 | 4730 | 417 | 9.4 | 483 | 77.2 | 3 | 30.7 | 54500 | 182
[21 empty] | W21x166 | 48.8 | 22.5 | 0.75 | 12.4 | 1.36 | 1.86 | 3.34 | 1.33 | 4280 | 380 | 9.36 | 435 | 70 | 2.99 | 23.6 | 48500 | 166
[21 empty] | W21x147 | 43.2 | 22.1 | 0.72 | 12.5 | 1.15 | 1.65 | 3.34 | 1.53 | 3630 | 329 | 9.17 | 376 | 60.1 | 2.95 | 15.4 | 41100 | 147
[21 empty] | W21x132 | 38.8 | 21.8 | 0.65 | 12.4 | 1.03 | 1.54 | 3.31 | 1.7 | 3220 | 295 | 9.12 | 333 | 53.5 | 2.93 | 11.3 | 36000 | 132
[21 empty] | W21x122 | 35.9 | 21.7 | 0.6 | 12.4 | 0.96 | 1.46 | 3.3 | 1.82 | 2960 | 273 | 9.09 | 305 | 49.2 | 2.92 | 8.98 | 32700 | 122
[21 empty] | W21x111 | 32.7 | 21.5 | 0.55 | 12.3 | 0.875 | 1.38 | 3.28 | 1.99 | 2670 | 249 | 9.05 | 274 | 44.5 | 2.9 | 6.83 | 29200 | 111
[21 empty] | W21x101 | 29.8 | 21.4 | 0.5 | 12.3 | 0.8 | 1.3 | 3.27 | 2.17 | 2420 | 227 | 9.02 | 248 | 40.3 | 2.89 | 5.21 | 26200 | 101
[21 empty] | W21x93 | 27.3 | 21.6 | 0.58 | 8.42 | 0.93 | 1.43 | 2.17 | 2.76 | 2070 | 192 | 8.7 | 92.9 | 22.1 | 1.84 | 6.03 | 9940 | 93
[21 empty] | W21x83 | 24.3 | 21.4 | 0.515 | 8.36 | 0.835 | 1.34 | 2.15 | 3.07 | 1830 | 171 | 8.67 | 81.4 | 19.5 | 1.83 | 4.34 | 8630 | 83
[21 empty] | W21x73 | 21.5 | 21.2 | 0.455 | 8.3 | 0.74 | 1.24 | 2.13 | 3.46 | 1600 | 151 | 8.64 | 70.6 | 17 | 1.81 | 3.02 | 7420 | 73
[21 empty] | W21x68 | 20 | 21.1 | 0.43 | 8.27 | 0.685 | 1.19 | 2.12 | 3.73 | 1480 | 140 | 8.6 | 64.7 | 15.7 | 1.8 | 2.45 | 6760 | 68
[21 empty] | W21x62 | 18.3 | 21 | 0.4 | 8.24 | 0.615 | 1.12 | 2.1 | 4.14 | 1330 | 127 | 8.54 | 57.5 | 14 | 1.77 | 1.83 | 5970 | 62
[21 empty] | W21x57 | 16.7 | 21.1 | 0.405 | 6.56 | 0.65 | 1.15 | 1.64 | 4.94 | 1170 | 111 | 8.36 | 30.6 | 9.35 | 1.35 | 1.77 | 3190 | 57
[21 empty] | W21x55 | 16.2 | 20.8 | 0.375 | 8.22 | 0.522 | 1.02 | 2.09 | 4.85 | 1140 | 110 | 8.4 | 48.4 | 11.8 | 1.73 | 1.24 | 4980 | 55
[21 empty] | W21x50 | 14.7 | 20.8 | 0.38 | 6.53 | 0.535 | 1.04 | 1.6 | 5.96 | 984 | 94.5 | 8.18 | 24.9 | 7.64 | 1.3 | 1.14 | 2560 | 50
[21 empty] | W21x48 | 14.1 | 20.6 | 0.35 | 8.14 | 0.43 | 0.93 | 2.04 | 5.89 | 959 | 93 | 8.24 | 38.7 | 9.52 | 1.66 | 0.803 | 3940 | 48
[21 empty] | W21x44 | 13 | 20.7 | 0.35 | 6.5 | 0.45 | 0.95 | 1.57 | 7.06 | 843 | 81.6 | 8.06 | 20.7 | 6.37 | 1.26 | 0.77 | 2110 | 44
[21 empty] | W18x311 | 91.5 | 22.32 | 1.52 | 12.005 | 2.74 | 3.4375 | 3.26 | 0.68 | 6960 | 624 | 8.72 | 795 | 132 | 2.95 | 177 | 75700 | 311
[21 empty] | W18x283 | 83.2 | 21.85 | 1.4 | 11.89 | 2.5 | 3.1875 | 3.23 | 0.74 | 6160 | 564 | 8.61 | 704 | 118 | 2.91 | 135 | 65600 | 283
[21 empty] | W18x258 | 75.9 | 21.46 | 1.28 | 11.77 | 2.3 | 3 | 3.19 | 0.79 | 5510 | 514 | 8.53 | 628 | 107 | 2.88 | 104 | 57400 | 258
[21 empty] | W18x234 | 68.8 | 21.06 | 1.16 | 11.65 | 2.11 | 2.75 | 3.16 | 0.86 | 4900 | 466 | 8.44 | 558 | 95.8 | 2.85 | 79.7 | 49900 | 234
[21 empty] | W18x211 | 62.1 | 20.67 | 1.06 | 11.555 | 1.91 | 2.5625 | 3.13 | 0.94 | 4330 | 419 | 8.35 | 493 | 85.3 | 2.82 | 59.3 | 43200 | 211
[21 empty] | W18x192 | 56.4 | 20.35 | 0.96 | 11.455 | 1.75 | 2.4375 | 3.1 | 1.02 | 3870 | 380 | 8.28 | 440 | 76.8 | 2.79 | 45.2 | 37900 | 192
[21 empty] | W18x175 | 51.3 | 20 | 0.89 | 11.4 | 1.59 | 1.99 | 3.07 | 1.11 | 3450 | 344 | 8.2 | 391 | 68.8 | 2.76 | 33.8 | 33300 | 175
[21 empty] | W18x158 | 46.3 | 19.7 | 0.81 | 11.3 | 1.44 | 1.84 | 3.05 | 1.21 | 3060 | 310 | 8.12 | 347 | 61.4 | 2.74 | 25.2 | 29000 | 158
[21 empty] | W18x143 | 42.1 | 19.5 | 0.73 | 11.2 | 1.32 | 1.72 | 3.03 | 1.32 | 2750 | 282 | 8.09 | 311 | 55.5 | 2.72 | 19.2 | 25700 | 143
[21 empty] | W18x130 | 38.2 | 19.3 | 0.67 | 11.2 | 1.2 | 1.6 | 3.01 | 1.44 | 2460 | 256 | 8.03 | 278 | 49.9 | 2.7 | 14.5 | 22600 | 130
[21 empty] | W18x119 | 35.1 | 19 | 0.655 | 11.3 | 1.06 | 1.46 | 3.02 | 1.59 | 2190 | 231 | 7.9 | 253 | 44.9 | 2.69 | 10.6 | 20300 | 119
[21 empty] | W18x106 | 31.1 | 18.7 | 0.59 | 11.2 | 0.94 | 1.34 | 3 | 1.78 | 1910 | 204 | 7.84 | 220 | 39.4 | 2.66 | 7.48 | 17400 | 106
[21 empty] | W18x97 | 28.5 | 18.6 | 0.535 | 11.1 | 0.87 | 1.27 | 2.99 | 1.92 | 1750 | 188 | 7.82 | 201 | 36.1 | 2.65 | 5.86 | 15800 | 97
[21 empty] | W18x86 | 25.3 | 18.4 | 0.48 | 11.1 | 0.77 | 1.17 | 2.97 | 2.15 | 1530 | 166 | 7.77 | 175 | 31.6 | 2.63 | 4.1 | 13600 | 86
[21 empty] | W18x76 | 22.3 | 18.2 | 0.425 | 11 | 0.68 | 1.08 | 2.95 | 2.43 | 1330 | 146 | 7.73 | 152 | 27.6 | 2.61 | 2.83 | 11700 | 76
[21 empty] | W18x71 | 20.8 | 18.5 | 0.495 | 7.64 | 0.81 | 1.21 | 1.98 | 2.99 | 1170 | 127 | 7.5 | 60.3 | 15.8 | 1.7 | 3.49 | 4700 | 71
[21 empty] | W18x65 | 19.1 | 18.4 | 0.45 | 7.59 | 0.75 | 1.15 | 1.97 | 3.22 | 1070 | 117 | 7.49 | 54.8 | 14.4 | 1.69 | 2.73 | 4240 | 65
[21 empty] | W18x60 | 17.6 | 18.2 | 0.415 | 7.56 | 0.695 | 1.1 | 1.96 | 3.47 | 984 | 108 | 7.47 | 50.1 | 13.3 | 1.68 | 2.17 | 3860 | 60
[21 empty] | W18x55 | 16.2 | 18.1 | 0.39 | 7.53 | 0.63 | 1.03 | 1.95 | 3.82 | 890 | 98.3 | 7.41 | 44.9 | 11.9 | 1.67 | 1.66 | 3430 | 55
[21 empty] | W18x50 | 14.7 | 18 | 0.355 | 7.5 | 0.57 | 0.972 | 1.94 | 4.21 | 800 | 88.9 | 7.38 | 40.1 | 10.7 | 1.65 | 1.24 | 3040 | 50
[21 empty] | W18x46 | 13.5 | 18.1 | 0.36 | 6.06 | 0.605 | 1.01 | 1.54 | 4.93 | 712 | 78.8 | 7.25 | 22.5 | 7.43 | 1.29 | 1.22 | 1710 | 46
[21 empty] | W18x40 | 11.8 | 17.9 | 0.315 | 6.02 | 0.525 | 0.927 | 1.52 | 5.67 | 612 | 68.4 | 7.21 | 19.1 | 6.35 | 1.27 | 0.81 | 1440 | 40
[21 empty] | W18x35 | 10.3 | 17.7 | 0.3 | 6 | 0.425 | 0.827 | 1.49 | 6.94 | 510 | 57.6 | 7.04 | 15.3 | 5.12 | 1.22 | 0.506 | 1140 | 35
[21 empty] | W16x100 | 29.7 | 17 | 0.585 | 10.4 | 0.985 | 1.69 | 2.81 | 1.65 | 1500 | 177 | 7.1 | 186 | 35.7 | 2.5 | 8.21 | 11900 | 100
[21 empty] | W16x89 | 26.4 | 16.8 | 0.525 | 10.4 | 0.875 | 1.58 | 2.79 | 1.85 | 1310 | 157 | 7.05 | 163 | 31.4 | 2.48 | 5.83 | 10300 | 89
[21 empty] | W16x77 | 22.9 | 16.5 | 0.455 | 10.3 | 0.76 | 1.47 | 2.77 | 2.11 | 1120 | 136 | 7 | 138 | 26.9 | 2.46 | 3.86 | 8570 | 77
[21 empty] | W16x67 | 20 | 16.3 | 0.395 | 10.2 | 0.665 | 1.37 | 2.75 | 2.4 | 970 | 119 | 6.97 | 119 | 23.2 | 2.44 | 2.62 | 7300 | 67
[21 empty] | W16x57 | 16.8 | 16.4 | 0.43 | 7.12 | 0.715 | 1.12 | 1.86 | 3.23 | 758 | 92.2 | 6.72 | 43.1 | 12.1 | 1.6 | 2.22 | 2660 | 57
[21 empty] | W16x50 | 14.7 | 16.3 | 0.38 | 7.07 | 0.63 | 1.03 | 1.84 | 3.65 | 659 | 81 | 6.68 | 37.2 | 10.5 | 1.59 | 1.52 | 2270 | 50
[21 empty] | W16x45 | 13.3 | 16.1 | 0.345 | 7.04 | 0.565 | 0.967 | 1.83 | 4.06 | 586 | 72.7 | 6.65 | 32.8 | 9.34 | 1.57 | 1.11 | 1990 | 45
[21 empty] | W16x40 | 11.8 | 16 | 0.305 | 7 | 0.505 | 0.907 | 1.82 | 4.53 | 518 | 64.7 | 6.63 | 28.9 | 8.25 | 1.57 | 0.794 | 1740 | 40
[21 empty] | W16x36 | 10.6 | 15.9 | 0.295 | 6.99 | 0.43 | 0.832 | 1.79 | 5.28 | 448 | 56.5 | 6.51 | 24.5 | 7 | 1.52 | 0.545 | 1460 | 36
[21 empty] | W16x31 | 9.13 | 15.9 | 0.275 | 5.53 | 0.44 | 0.842 | 1.39 | 6.53 | 375 | 47.2 | 6.41 | 12.4 | 4.49 | 1.17 | 0.461 | 739 | 31
[21 empty] | W16x26 | 7.68 | 15.7 | 0.25 | 5.5 | 0.345 | 0.747 | 1.36 | 8.27 | 301 | 38.4 | 6.26 | 9.59 | 3.49 | 1.12 | 0.262 | 565 | 26
[21 empty] | W14x808 | 237 | 22.8 | 3.74 | 18.6 | 5.12 | 5.72 | 5.15 | 0.24 | 16000 | 1400 | 8.2 | 5510 | 594 | 4.82 | 1840 | 433000 | 808
[21 empty] | W14x730 | 215 | 22.4 | 3.07 | 17.9 | 4.91 | 5.51 | 4.99 | 0.26 | 14300 | 1280 | 8.17 | 4720 | 527 | 4.69 | 1450 | 362000 | 730
[21 empty] | W14x665 | 196 | 21.6 | 2.83 | 17.7 | 4.52 | 5.12 | 4.92 | 0.27 | 12400 | 1150 | 7.98 | 4170 | 472 | 4.62 | 1120 | 306000 | 665
[21 empty] | W14x605 | 178 | 20.9 | 2.6 | 17.4 | 4.16 | 4.76 | 4.85 | 0.29 | 10800 | 1040 | 7.8 | 3680 | 423 | 4.55 | 869 | 258000 | 605
[21 empty] | W14x550 | 162 | 20.2 | 2.38 | 17.2 | 3.82 | 4.42 | 4.79 | 0.31 | 9430 | 931 | 7.63 | 3250 | 378 | 4.49 | 669 | 219000 | 550
[21 empty] | W14x500 | 147 | 19.6 | 2.19 | 17 | 3.5 | 4.1 | 4.73 | 0.33 | 8210 | 838 | 7.48 | 2880 | 339 | 4.43 | 514 | 187000 | 500
[21 empty] | W14x455 | 134 | 19 | 2.02 | 16.8 | 3.21 | 3.81 | 4.68 | 0.35 | 7190 | 756 | 7.33 | 2560 | 304 | 4.38 | 395 | 160000 | 455
[21 empty] | W14x426 | 125 | 18.7 | 1.88 | 16.7 | 3.04 | 3.63 | 4.64 | 0.37 | 6600 | 706 | 7.26 | 2360 | 283 | 4.34 | 331 | 144000 | 426
[21 empty] | W14x398 | 117 | 18.3 | 1.77 | 16.6 | 2.85 | 3.44 | 4.61 | 0.39 | 6000 | 656 | 7.16 | 2170 | 262 | 4.31 | 273 | 129000 | 398
[21 empty] | W14x370 | 109 | 17.9 | 1.66 | 16.5 | 2.66 | 3.26 | 4.57 | 0.41 | 5440 | 607 | 7.07 | 1990 | 241 | 4.27 | 222 | 116000 | 370
[21 empty] | W14x342 | 101 | 17.5 | 1.54 | 16.4 | 2.47 | 3.07 | 4.54 | 0.43 | 4900 | 558 | 6.98 | 1810 | 221 | 4.24 | 178 | 103000 | 342
[21 empty] | W14x311 | 91.4 | 17.1 | 1.41 | 16.2 | 2.26 | 2.86 | 4.5 | 0.47 | 4330 | 506 | 6.88 | 1610 | 199 | 4.2 | 136 | 88900 | 311
[21 empty] | W14x283 | 83.3 | 16.7 | 1.29 | 16.1 | 2.07 | 2.67 | 4.46 | 0.5 | 3840 | 459 | 6.79 | 1440 | 179 | 4.17 | 104 | 77500 | 283
[21 empty] | W14x257 | 75.6 | 16.4 | 1.18 | 16 | 1.89 | 2.49 | 4.43 | 0.54 | 3400 | 415 | 6.71 | 1290 | 161 | 4.13 | 79.1 | 67700 | 257
[21 empty] | W14x233 | 68.5 | 16 | 1.07 | 15.9 | 1.72 | 2.32 | 4.4 | 0.59 | 3010 | 375 | 6.63 | 1150 | 145 | 4.1 | 59.5 | 59000 | 233
[21 empty] | W14x211 | 62 | 15.7 | 0.98 | 15.8 | 1.56 | 2.16 | 4.37 | 0.64 | 2660 | 338 | 6.55 | 1030 | 130 | 4.07 | 44.6 | 51600 | 211
[21 empty] | W14x193 | 56.8 | 15.5 | 0.89 | 15.7 | 1.44 | 2.04 | 4.35 | 0.68 | 2400 | 310 | 6.5 | 931 | 119 | 4.05 | 34.8 | 45900 | 193
[21 empty] | W14x176 | 51.8 | 15.2 | 0.83 | 15.7 | 1.31 | 1.91 | 4.32 | 0.74 | 2140 | 281 | 6.43 | 838 | 107 | 4.02 | 26.5 | 40500 | 176
[21 empty] | W14x159 | 46.7 | 15 | 0.745 | 15.6 | 1.19 | 1.79 | 4.3 | 0.81 | 1900 | 254 | 6.38 | 748 | 96.2 | 4 | 19.7 | 35600 | 159
[21 empty] | W14x145 | 42.7 | 14.8 | 0.68 | 15.5 | 1.09 | 1.69 | 4.28 | 0.87 | 1710 | 232 | 6.33 | 677 | 87.3 | 3.98 | 15.2 | 31700 | 145
[21 empty] | W14x132 | 38.8 | 14.7 | 0.645 | 14.7 | 1.03 | 1.63 | 4.05 | 0.97 | 1530 | 209 | 6.28 | 548 | 74.5 | 3.76 | 12.3 | 25500 | 132
[21 empty] | W14x120 | 35.3 | 14.5 | 0.59 | 14.7 | 0.94 | 1.54 | 4.04 | 1.05 | 1380 | 190 | 6.24 | 495 | 67.5 | 3.74 | 9.37 | 22700 | 120
[21 empty] | W14x109 | 32 | 14.3 | 0.525 | 14.6 | 0.86 | 1.46 | 4.02 | 1.14 | 1240 | 173 | 6.22 | 447 | 61.2 | 3.73 | 7.12 | 20200 | 109
[21 empty] | W14x99 | 29.1 | 14.2 | 0.485 | 14.6 | 0.78 | 1.38 | 4 | 1.25 | 1110 | 157 | 6.17 | 402 | 55.2 | 3.71 | 5.37 | 18000 | 99
[21 empty] | W14x90 | 26.5 | 14 | 0.44 | 14.5 | 0.71 | 1.31 | 3.99 | 1.36 | 999 | 143 | 6.14 | 362 | 49.9 | 3.7 | 4.06 | 16000 | 90
[21 empty] | W14x82 | 24 | 14.3 | 0.51 | 10.1 | 0.855 | 1.45 | 2.74 | 1.65 | 881 | 123 | 6.05 | 148 | 29.3 | 2.48 | 5.07 | 6700 | 82
[21 empty] | W14x74 | 21.8 | 14.2 | 0.45 | 10.1 | 0.785 | 1.38 | 2.72 | 1.79 | 795 | 112 | 6.04 | 134 | 26.6 | 2.48 | 3.87 | 6000 | 74
[21 empty] | W14x68 | 20 | 14 | 0.415 | 10 | 0.72 | 1.31 | 2.71 | 1.94 | 722 | 103 | 6.01 | 121 | 24.2 | 2.46 | 3.01 | 5370 | 68
[21 empty] | W14x61 | 17.9 | 13.9 | 0.375 | 9.99 | 0.645 | 1.24 | 2.7 | 2.15 | 640 | 92.1 | 5.98 | 107 | 21.5 | 2.45 | 2.19 | 4690 | 61
[21 empty] | W14x53 | 15.6 | 13.9 | 0.37 | 8.06 | 0.66 | 1.25 | 2.15 | 2.62 | 541 | 77.8 | 5.89 | 57.7 | 14.3 | 1.92 | 1.94 | 2540 | 53
[21 empty] | W14x48 | 14.1 | 13.8 | 0.34 | 8.03 | 0.595 | 1.19 | 2.13 | 2.89 | 484 | 70.2 | 5.85 | 51.4 | 12.8 | 1.91 | 1.45 | 2240 | 48
[21 empty] | W14x43 | 12.6 | 13.7 | 0.305 | 8 | 0.53 | 1.12 | 2.12 | 3.22 | 428 | 62.6 | 5.82 | 45.2 | 11.3 | 1.89 | 1.05 | 1950 | 43
[21 empty] | W14x38 | 11.2 | 14.1 | 0.31 | 6.77 | 0.515 | 0.915 | 1.77 | 4.04 | 385 | 54.6 | 5.87 | 26.7 | 7.88 | 1.55 | 0.798 | 1230 | 38
[21 empty] | W14x34 | 10 | 14 | 0.285 | 6.75 | 0.455 | 0.855 | 1.76 | 4.56 | 340 | 48.6 | 5.83 | 23.3 | 6.91 | 1.53 | 0.569 | 1070 | 34
[21 empty] | W14x30 | 8.85 | 13.8 | 0.27 | 6.73 | 0.385 | 0.785 | 1.74 | 5.34 | 291 | 42 | 5.73 | 19.6 | 5.82 | 1.49 | 0.38 | 887 | 30
[21 empty] | W14x26 | 7.69 | 13.9 | 0.255 | 5.03 | 0.42 | 0.82 | 1.28 | 6.59 | 245 | 35.3 | 5.65 | 8.91 | 3.55 | 1.08 | 0.358 | 405 | 26
[21 empty] | W14x22 | 6.49 | 13.7 | 0.23 | 5 | 0.335 | 0.735 | 1.25 | 8.2 | 199 | 29 | 5.54 | 7 | 2.8 | 1.04 | 0.208 | 314 | 22
[21 empty] | W12x336 | 98.8 | 16.8 | 1.78 | 13.4 | 2.96 | 3.55 | 3.71 | 0.43 | 4060 | 483 | 6.41 | 1190 | 177 | 3.47 | 243 | 57200 | 336
[21 empty] | W12x305 | 89.6 | 16.3 | 1.63 | 13.2 | 2.71 | 3.3 | 3.67 | 0.46 | 3550 | 435 | 6.29 | 1050 | 159 | 3.42 | 185 | 48700 | 305
[21 empty] | W12x279 | 81.9 | 15.9 | 1.53 | 13.1 | 2.47 | 3.07 | 3.64 | 0.49 | 3110 | 393 | 6.16 | 937 | 143 | 3.38 | 143 | 41900 | 279
[21 empty] | W12x252 | 74 | 15.4 | 1.4 | 13 | 2.25 | 2.85 | 3.59 | 0.53 | 2720 | 353 | 6.06 | 828 | 127 | 3.34 | 108 | 35800 | 252
[21 empty] | W12x230 | 67.7 | 15.1 | 1.29 | 12.9 | 2.07 | 2.67 | 3.56 | 0.56 | 2420 | 321 | 5.97 | 742 | 115 | 3.31 | 83.8 | 31300 | 230
[21 empty] | W12x210 | 61.8 | 14.7 | 1.18 | 12.8 | 1.9 | 2.5 | 3.53 | 0.61 | 2140 | 292 | 5.89 | 664 | 104 | 3.28 | 64.7 | 27200 | 210
[21 empty] | W12x190 | 55.8 | 14.4 | 1.06 | 12.7 | 1.74 | 2.33 | 3.5 | 0.65 | 1890 | 263 | 5.82 | 589 | 93 | 3.25 | 48.8 | 23500 | 190
[21 empty] | W12x170 | 50 | 14 | 0.96 | 12.6 | 1.56 | 2.16 | 3.47 | 0.72 | 1650 | 235 | 5.74 | 517 | 82.3 | 3.22 | 35.6 | 20100 | 170
[21 empty] | W12x152 | 44.7 | 13.7 | 0.87 | 12.5 | 1.4 | 2 | 3.44 | 0.78 | 1430 | 209 | 5.66 | 454 | 72.8 | 3.19 | 25.8 | 17200 | 152
[21 empty] | W12x136 | 39.9 | 13.4 | 0.79 | 12.4 | 1.25 | 1.85 | 3.41 | 0.87 | 1240 | 186 | 5.58 | 398 | 64.2 | 3.16 | 18.5 | 14700 | 136
[21 empty] | W12x120 | 35.3 | 13.1 | 0.71 | 12.3 | 1.11 | 1.7 | 3.38 | 0.96 | 1070 | 163 | 5.51 | 345 | 56 | 3.13 | 12.9 | 12500 | 120
[21 empty] | W12x106 | 31.2 | 12.9 | 0.61 | 12.2 | 0.99 | 1.59 | 3.36 | 1.07 | 933 | 145 | 5.47 | 301 | 49.3 | 3.11 | 9.13 | 10700 | 106
[21 empty] | W12x96 | 28.2 | 12.7 | 0.55 | 12.2 | 0.9 | 1.5 | 3.34 | 1.16 | 833 | 131 | 5.44 | 270 | 44.4 | 3.09 | 6.85 | 9410 | 96
[21 empty] | W12x87 | 25.6 | 12.5 | 0.515 | 12.1 | 0.81 | 1.41 | 3.32 | 1.28 | 740 | 118 | 5.38 | 241 | 39.7 | 3.07 | 5.1 | 8280 | 87
[21 empty] | W12x79 | 23.2 | 12.4 | 0.47 | 12.1 | 0.735 | 1.33 | 3.31 | 1.39 | 662 | 107 | 5.34 | 216 | 35.8 | 3.05 | 3.84 | 7320 | 79
[21 empty] | W12x72 | 21.1 | 12.3 | 0.43 | 12 | 0.67 | 1.27 | 3.29 | 1.52 | 597 | 97.4 | 5.31 | 195 | 32.4 | 3.04 | 2.93 | 6540 | 72
[21 empty] | W12x65 | 19.1 | 12.1 | 0.39 | 12 | 0.605 | 1.2 | 3.28 | 1.67 | 533 | 87.9 | 5.28 | 174 | 29.1 | 3.02 | 2.18 | 5770 | 65
[21 empty] | W12x58 | 17 | 12.2 | 0.36 | 10 | 0.64 | 1.24 | 2.72 | 1.9 | 475 | 78 | 5.28 | 107 | 21.4 | 2.51 | 2.1 | 3570 | 58
[21 empty] | W12x53 | 15.6 | 12.1 | 0.345 | 9.99 | 0.575 | 1.17 | 2.71 | 2.1 | 425 | 70.6 | 5.23 | 95.8 | 19.2 | 2.48 | 1.58 | 3160 | 53
[21 empty] | W12x50 | 14.6 | 12.2 | 0.37 | 8.08 | 0.64 | 1.14 | 2.17 | 2.36 | 391 | 64.2 | 5.18 | 56.3 | 13.9 | 1.96 | 1.71 | 1880 | 50
[21 empty] | W12x45 | 13.1 | 12.1 | 0.335 | 8.05 | 0.575 | 1.08 | 2.15 | 2.61 | 348 | 57.7 | 5.15 | 50 | 12.4 | 1.95 | 1.26 | 1650 | 45
[21 empty] | W12x40 | 11.7 | 11.9 | 0.295 | 8.01 | 0.515 | 1.02 | 2.14 | 2.9 | 307 | 51.5 | 5.13 | 44.1 | 11 | 1.94 | 0.906 | 1440 | 40
[21 empty] | W12x35 | 10.3 | 12.5 | 0.3 | 6.56 | 0.52 | 0.82 | 1.74 | 3.66 | 285 | 45.6 | 5.25 | 24.5 | 7.47 | 1.54 | 0.741 | 879 | 35
[21 empty] | W12x30 | 8.79 | 12.3 | 0.26 | 6.52 | 0.44 | 0.74 | 1.73 | 4.3 | 238 | 38.6 | 5.21 | 20.3 | 6.24 | 1.52 | 0.457 | 719 | 30
[21 empty] | W12x26 | 7.65 | 12.2 | 0.23 | 6.49 | 0.38 | 0.68 | 1.72 | 4.95 | 204 | 33.4 | 5.17 | 17.3 | 5.34 | 1.51 | 0.3 | 606 | 26
[21 empty] | W12x22 | 6.48 | 12.3 | 0.26 | 4.03 | 0.425 | 0.725 | 1.02 | 7.19 | 156 | 25.4 | 4.91 | 4.66 | 2.31 | 0.848 | 0.293 | 165 | 22
[21 empty] | W12x19 | 5.57 | 12.2 | 0.235 | 4.01 | 0.35 | 0.65 | 1 | 8.67 | 130 | 21.3 | 4.82 | 3.76 | 1.88 | 0.822 | 0.18 | 131 | 19
[21 empty] | W12x16 | 4.71 | 12 | 0.22 | 3.99 | 0.265 | 0.565 | 0.96 | 11.3 | 103 | 17.1 | 4.67 | 2.82 | 1.41 | 0.773 | 0.103 | 96.9 | 16
[21 empty] | W12x14 | 4.16 | 11.9 | 0.2 | 3.97 | 0.225 | 0.525 | 0.95 | 13.3 | 88.6 | 14.9 | 4.62 | 2.36 | 1.19 | 0.753 | 0.0704 | 80.6 | 14
[21 empty] | W10x112 | 32.9 | 11.4 | 0.755 | 10.4 | 1.25 | 1.75 | 2.88 | 0.87 | 716 | 126 | 4.66 | 236 | 45.3 | 2.68 | 15.1 | 6030 | 112
[21 empty] | W10x100 | 29.4 | 11.1 | 0.68 | 10.3 | 1.12 | 1.62 | 2.85 | 0.96 | 623 | 112 | 4.6 | 207 | 40 | 2.65 | 10.9 | 5150 | 100
[21 empty] | W10x88 | 25.9 | 10.8 | 0.605 | 10.3 | 0.99 | 1.49 | 2.83 | 1.07 | 534 | 98.5 | 4.54 | 179 | 34.8 | 2.63 | 7.53 | 4340 | 88
[21 empty] | W10x77 | 22.6 | 10.6 | 0.53 | 10.2 | 0.87 | 1.37 | 2.8 | 1.2 | 455 | 85.9 | 4.49 | 154 | 30.1 | 2.6 | 5.11 | 3640 | 77
[21 empty] | W10x68 | 20 | 10.4 | 0.47 | 10.1 | 0.77 | 1.27 | 2.79 | 1.33 | 394 | 75.7 | 4.44 | 134 | 26.4 | 2.59 | 3.56 | 3110 | 68
[21 empty] | W10x60 | 17.6 | 10.2 | 0.42 | 10.1 | 0.68 | 1.18 | 2.77 | 1.49 | 341 | 66.7 | 4.39 | 116 | 23 | 2.57 | 2.48 | 2640 | 60
[21 empty] | W10x54 | 15.8 | 10.1 | 0.37 | 10 | 0.615 | 1.12 | 2.75 | 1.64 | 303 | 60 | 4.37 | 103 | 20.6 | 2.56 | 1.82 | 2310 | 54
[21 empty] | W10x49 | 14.4 | 9.98 | 0.34 | 10 | 0.56 | 1.06 | 2.74 | 1.78 | 272 | 54.6 | 4.35 | 93.4 | 18.7 | 2.54 | 1.39 | 2070 | 49
[21 empty] | W10x45 | 13.3 | 10.1 | 0.35 | 8.02 | 0.62 | 1.12 | 2.18 | 2.03 | 248 | 49.1 | 4.32 | 53.4 | 13.3 | 2.01 | 1.51 | 1200 | 45
[21 empty] | W10x39 | 11.5 | 9.92 | 0.315 | 7.99 | 0.53 | 1.03 | 2.16 | 2.34 | 209 | 42.1 | 4.27 | 45 | 11.3 | 1.98 | 0.976 | 992 | 39
[21 empty] | W10x33 | 9.71 | 9.73 | 0.29 | 7.96 | 0.435 | 0.935 | 2.14 | 2.81 | 171 | 35 | 4.19 | 36.6 | 9.2 | 1.94 | 0.583 | 791 | 33
[21 empty] | W10x30 | 8.84 | 10.5 | 0.3 | 5.81 | 0.51 | 0.81 | 1.55 | 3.53 | 170 | 32.4 | 4.38 | 16.7 | 5.75 | 1.37 | 0.622 | 414 | 30
[21 empty] | W10x26 | 7.61 | 10.3 | 0.26 | 5.77 | 0.44 | 0.74 | 1.54 | 4.07 | 144 | 27.9 | 4.35 | 14.1 | 4.89 | 1.36 | 0.402 | 345 | 26
[21 empty] | W10x22 | 6.49 | 10.2 | 0.24 | 5.75 | 0.36 | 0.66 | 1.51 | 4.91 | 118 | 23.2 | 4.27 | 11.4 | 3.97 | 1.33 | 0.239 | 274 | 22
[21 empty] | W10x19 | 5.62 | 10.2 | 0.25 | 4.02 | 0.395 | 0.695 | 1.03 | 6.45 | 96.3 | 18.8 | 4.14 | 4.29 | 2.14 | 0.874 | 0.233 | 104 | 19
[21 empty] | W10x17 | 4.99 | 10.1 | 0.24 | 4.01 | 0.33 | 0.63 | 1.01 | 7.64 | 81.9 | 16.2 | 4.05 | 3.56 | 1.78 | 0.845 | 0.156 | 85.1 | 17
[21 empty] | W10x15 | 4.41 | 9.99 | 0.23 | 4 | 0.27 | 0.57 | 0.99 | 9.25 | 68.9 | 13.8 | 3.95 | 2.89 | 1.45 | 0.81 | 0.104 | 68.3 | 15
[21 empty] | W10x12 | 3.54 | 9.87 | 0.19 | 3.96 | 0.21 | 0.51 | 0.96 | 11.9 | 53.8 | 10.9 | 3.9 | 2.18 | 1.1 | 0.785 | 0.0547 | 50.9 | 12
[21 empty] | W8x67 | 19.7 | 9 | 0.57 | 8.28 | 0.935 | 1.33 | 2.28 | 1.16 | 272 | 60.4 | 3.72 | 88.6 | 21.4 | 2.12 | 5.05 | 1440 | 67
[21 empty] | W8x58 | 17.1 | 8.75 | 0.51 | 8.22 | 0.81 | 1.2 | 2.26 | 1.31 | 228 | 52 | 3.65 | 75.1 | 18.3 | 2.1 | 3.33 | 1180 | 58
[21 empty] | W8x48 | 14.1 | 8.5 | 0.4 | 8.11 | 0.685 | 1.08 | 2.23 | 1.53 | 184 | 43.2 | 3.61 | 60.9 | 15 | 2.08 | 1.96 | 930 | 48
[21 empty] | W8x40 | 11.7 | 8.25 | 0.36 | 8.07 | 0.56 | 0.954 | 2.21 | 1.83 | 146 | 35.5 | 3.53 | 49.1 | 12.2 | 2.04 | 1.12 | 726 | 40
[21 empty] | W8x35 | 10.3 | 8.12 | 0.31 | 8.02 | 0.495 | 0.889 | 2.2 | 2.05 | 127 | 31.2 | 3.51 | 42.6 | 10.6 | 2.03 | 0.769 | 619 | 35
[21 empty] | W8x31 | 9.12 | 8 | 0.285 | 8 | 0.435 | 0.829 | 2.18 | 2.3 | 110 | 27.5 | 3.47 | 37.1 | 9.27 | 2.02 | 0.536 | 531 | 31
[21 empty] | W8x28 | 8.24 | 8.06 | 0.285 | 6.54 | 0.465 | 0.859 | 1.77 | 2.65 | 98 | 24.3 | 3.45 | 21.7 | 6.63 | 1.62 | 0.537 | 313 | 28
[21 empty] | W8x24 | 7.08 | 7.93 | 0.245 | 6.5 | 0.4 | 0.794 | 1.76 | 3.05 | 82.7 | 20.9 | 3.42 | 18.3 | 5.63 | 1.61 | 0.346 | 259 | 24
[21 empty] | W8x21 | 6.16 | 8.28 | 0.25 | 5.27 | 0.4 | 0.7 | 1.41 | 3.93 | 75.3 | 18.2 | 3.49 | 9.77 | 3.71 | 1.26 | 0.282 | 152 | 21
[21 empty] | W8x18 | 5.26 | 8.14 | 0.23 | 5.25 | 0.33 | 0.63 | 1.39 | 4.7 | 61.9 | 15.2 | 3.43 | 7.97 | 3.04 | 1.23 | 0.172 | 122 | 18
[21 empty] | W8x15 | 4.44 | 8.11 | 0.245 | 4.01 | 0.315 | 0.615 | 1.03 | 6.41 | 48 | 11.8 | 3.29 | 3.41 | 1.7 | 0.876 | 0.137 | 51.8 | 15
[21 empty] | W8x13 | 3.84 | 7.99 | 0.23 | 4 | 0.255 | 0.555 | 1.01 | 7.83 | 39.6 | 9.91 | 3.21 | 2.73 | 1.37 | 0.843 | 0.0871 | 40.8 | 13
[21 empty] | W8x10 | 2.96 | 7.89 | 0.17 | 3.94 | 0.205 | 0.505 | 0.99 | 9.77 | 30.8 | 7.81 | 3.22 | 2.09 | 1.06 | 0.841 | 0.0426 | 30.9 | 10
[21 empty] | W6x25 | 7.36 | 6.38 | 0.32 | 6.08 | 0.455 | 0.754 | 1.66 | 2.31 | 53.6 | 16.8 | 2.7 | 17.1 | 5.61 | 1.52 | 0.47 | 150 | 25
[21 empty] | W6x20 | 5.89 | 6.2 | 0.26 | 6.02 | 0.365 | 0.664 | 1.64 | 2.82 | 41.5 | 13.4 | 2.66 | 13.3 | 4.41 | 1.5 | 0.246 | 113 | 20
[21 empty] | W6x16 | 4.74 | 6.28 | 0.26 | 4.03 | 0.405 | 0.655 | 1.08 | 3.85 | 32.1 | 10.2 | 2.6 | 4.43 | 2.2 | 0.967 | 0.223 | 38.2 | 16
[21 empty] | W6x15 | 4.45 | 5.99 | 0.23 | 5.99 | 0.26 | 0.559 | 1.61 | 3.85 | 29.3 | 9.77 | 2.56 | 9.32 | 3.11 | 1.45 | 0.105 | 76.5 | 15
[21 empty] | W6x12 | 3.55 | 6.03 | 0.23 | 4 | 0.28 | 0.53 | 1.05 | 5.38 | 22.1 | 7.31 | 2.49 | 2.99 | 1.5 | 0.918 | 0.0903 | 24.7 | 12
[21 empty] | W6x9 | 2.68 | 5.9 | 0.17 | 3.94 | 0.215 | 0.465 | 1.03 | 6.96 | 16.4 | 5.56 | 2.47 | 2.2 | 1.11 | 0.905 | 0.0405 | 17.8 | 9
[21 empty] | W6x8.5 | 2.51 | 5.83 | 0.17 | 3.94 | 0.194 | 0.444 | 1.038 | 7.63 | 14.8 | 5.08 | 2.43 | 1.98 | 1.01 | 0.889 | 0.033 | 15.7 | 8.5
[21 empty] | W5x19 | 5.56 | 5.15 | 0.27 | 5.03 | 0.43 | 0.73 | 1.38 | 2.38 | 26.3 | 10.2 | 2.17 | 9.13 | 3.63 | 1.28 | 0.316 | 50.9 | 19
[21 empty] | W5x16 | 4.71 | 5.01 | 0.24 | 5 | 0.36 | 0.66 | 1.37 | 2.78 | 21.4 | 8.55 | 2.13 | 7.51 | 3 | 1.26 | 0.192 | 40.6 | 16
[21 empty] | W4x13 | 3.83 | 4.16 | 0.28 | 4.06 | 0.345 | 0.595 | 1.1 | 2.97 | 11.3 | 5.46 | 1.72 | 3.86 | 1.9 | 1 | 0.151 | 14 | 13
Note on BA1: "MONORAIL.xls" written by: Alex Tomanovich, P.E.
Note on BC26: If this user elects to use this reference for the analysis of the overhang (cantilever) portion of the monorail beam, then this value of Lbo = Lo+L should be input into cell C17.
Note on BC28: If this user elects to use this reference for the analysis of the overhang (cantilever) portion of the monorail beam, then this computed value of 'Cbo', interpolated from Table 1, should be input into cell C18.
Note on BG26: Table 1 is reproduced from page 137 of the referenced article.
Note on F28: For a monorail consisting of a simple-span with no overhang, 'RR(max)' and 'RL(min)' are determined by positioning the trolley at the right support. For a monorail consisting of a simple-span with an overhang, 'RR(max)' and 'RL(min)' are determined by positioning the trolley at the end of the overhang. The self-weight of the monorail beam is also included.
Note on F29: For a monorail consisting of a simple-span with no overhang, 'RR(max)' and 'RL(min)' are determined by positioning the trolley at the right support. For a monorail consisting of a simple-span with an overhang, 'RR(max)' and 'RL(min)' are determined by positioning the trolley at the end of the overhang. The self-weight of the monorail beam is also included.
Note on C17: The unbraced length for the overhang (cantilever) portion, 'Lbo', is often debated. Here are some recommendations from different sources: 1. Per Fluor Enterprises Guideline 000.215.1257 - "Hoisting Facilities" Lbo = Lo+L/2 2. Per Dupont Standard DB1X - "Design and Installation of Monorail Beams" Lbo = 3*Lo 3. Per ANSI MH27.1 - "Underhung Cranes and Monorail Systems" Lbo = 2*Lo 4. Per British Steel Code B.S. 449, pages 42-44 (1959) Lbo = 2*Lo (for top flange of monorail beam restrained at support) Lbo = 3*Lo (for top flange of monorail beam unrestrained at support) 5. Per AISC Journal article by N. Stephen Tanner - "Allowable Bending Stresses for Overhanging Monorails" (3rd Quarter, 1985) Lbo = Lo+L (used with a computed value of 'Cbo' from article)
Note on C15: From AISC 9th Edition ASD Manual, page 5-47: 'Cb' is the allowable stress bending coefficient dependent on the moment gradient, for bending about the X-axis (major axis). 'Cb' is determined as follows: Cb = 1.75+1.05*(Mx1/Mx2)+0.3*(Mx1/Mx2)^2 <= 2.3 where: Mx1 = smaller X-axis (major axis) bending moment at either of the ends of the unbraced length Mx2 = larger X-axis (major axis) bending moment at either of the ends of the unbraced length Mx1/Mx2 = positive for reverse curvature bending (both have same signs) = negative for single curvature bending (both have opposite signs) Note: 1. When the bending moment at any point within an unbraced length is larger than that at both ends of this length, then use 'Cb' = 1.0.
Note on B70: Note: a Vertical Deflection criteria of L/450 is assumed to be used, and is taken from CMAA Specification No. 74, per Section 1.4.1.2 for "Under-Running Runways".
tw
Pw
Pw
Point 2
Point 1
Point 0
bf
tf
Y
Z
X